## EqCircut
.
What is the % BDT before Correlation ? |  |  |  | 214.4 |  |  | Voltage : |  | 460 | First Cycle Inrush
What is the % BDT after Correlation ? |  |  |  | 283.0 |  |  | Frequency : |  | 60 | 2.35
[7 empty] | No-Load Current: |  | 77.45 / 107.93
what are the No Load Amps? |  |  | 07.93 |  |  |  | Full Load Current: |  | 277.74 / 295.13
[7 empty] | Breakdown Torque: |  | 214.4 / 283.0
What are the Full load Amps? |  |  | 295.13 |  |  |  | Wc: |  | 4161.8 / 2057.4
[7 empty] | Wf: |  | 980.0 / 979.7
TOSHIBA INTERNATIONAL CORPORATION
ALL VALUES ARE IN EQULIVALENT Y
|  |  | VALUE (OHMS) |  | PER UNIT
BASE IMPEDANCE PER UNIT |  |  | 0.89988 |  | 1
PRIMARY REISTANCE (R1) |  |  | 0.0051792 |  | 0.0057555
SECONDARY RESISTANCE (R2) |  |  | 0.0061107 |  | 0.0067906 |  |  | Project or Lab:
STARTING RESISTANCE (R3) |  |  | 0.032671 |  | 0.036306 |  |  | RF2500
PRIMARY REACTANCE (X1) |  |  | 0.052374 |  | 0.058201
SECONDARY REACTANCE (X2) |  |  | 0.1293 |  | 0.14369
STARTING REACTANCE (X3) |  |  | 0.092416 |  | 0.1027
MAGNETIZING REACTANCE (XM) |  |  | 33.4907 |  | 37.2169
TRANSIENT REACTANCE (Xd') |  |  | 0.18118 |  | 0.20134
SUB TRANSIENT REACTANCE (Xd") |  |  | 0.10618 |  | 0.118
SHORT CIRCUIT TIME CONSTANT |  |  | 0.078827 |  | 0.087597
SUB TRANSIENT TIME CONSTANT |  |  | 0.010527 |  | 0.011698
OPEN CIRCUIT TIME CONSTANT |  |  | 14.594 |  | 16.2177
INDUCTANCES (HENRIES)
STATOR INDUCTANCE (L1) |  |  | 0.00013893 |  | 0.00015438
ROTOR INDUCTANCE (L2) |  |  | 0.00034298 |  | 0.00038114
STARTING INDUCTANCE (L3) |  |  | 0.00024514 |  | 0.00027242
Rev.1 Added Starting Reactance. 11/18/04 MDC
Rev.2 Corrections to calculations & added first cycle inrush 1/28/09 JR & MDC
Rev.3 Corrected Calculation for R3 MDC 12/9/09
Rev.4 Correction to short circuit time constant. |  |  |  |  | Used to be "=(B57+((B56*B61)/(B56 * B61))/(B51*E41))" |  |  |  |  | Z.X 10/25/2019
Rev.5 Correction to short circuit time contstant. Used to be "=(B57+((B56*B61)/(B56+B61))/(B51*E41))" Z.X 12/14/2021
2*pi*f
| Jcon = | 3 | Wo = | 376.9911 | Xcorr = | .666666666666666666666666
| X BDT = | 1.32
pacop = | 8.1768 |  | Xcorr * Coil End Reactance
pacop2= | 4.0884 |  | (1-Xcorr) * Coil End Reactance
pac11p = | 8.1768 |  | Xcorr * Coil End Reactance
pac12p = | 4.0884 |  | (1-Xcorr) * Coil End Reactance
base = | 0.89988 |  | Impedance (not used)
r1 = | 0.0051792 |  | Primary Resistance
r2 = | 0.0061107 |  | Seconadry Resistance
r3 = | 0.032671 |  | Starting Secondary Resistance
xs = | 0.54502 |  | Total Reactance
x1r = | 37.1122 |  | Stator Slot Reactance + 1/2 Zigzag Reactance + 1/2 Belt Leakage Reactance + Xcorr * Coil End Reactance
x2r = | 91.6229 |  | Rotor Slot Reactance + 1/2 Zigzag Reactance + 1/2 Belt Leakage Reactance + (1-Xcorr) * Coil End Reactance
x1 = | 0.052374 |  | Primary Reactance
x2 = | 0.1293 |  | Secondary Reactance
x1s = | 10.7178 |  | [Starting Stator Slot Reactance + 1/2 Starting Zigzag Reactance + Xcorr * Coil End Reactance] / Jconn
x2s = | 15.0883 |  | [Starting Rotor Slot Reactance + 1/2 Starting Zigzag Reactance + (1-Xcorr) * Coil End Reactance] / Jconn
x3 = | 0.092416 |  | Starting Rotor Reactance
xm= | 33.4907 |  | Magnetizing Reactance
tx = | 0.18118 |  | Transient Reactance = Primary Reactance + Secondary Reactance // Magnetizing Reactance
stx = | 0.10618 |  | Sub Transient Reactance = Primary Reactance + Secondary Reactance // Magnetizing Reactance // Starting Secondary Reactance | [7 empty] | ???
sctc = | 0.078827 |  | Short circuit time constant = (X2 + X1//Xm) / (2*pi*f * r2)
sttc = | 0.010527 |  | sub transient time constant = (X3 + X1//X2//Xm) / (2*pi*f * r3)
octo = | 14.594 |  | open circuit time constant = (Xm + X2) / (2*pi*f * r2)
l1 = | 0.00013893 |  | Primary Inductance
l2 = | 0.00034298 |  | Secondary Inductance
l3 = | 0.00024514 |  | Starting Rotor Inductance
NEMA MG1 way of short circuit AC time constant
sctc = | 0.078827 |  | Short circuit time constant = (X1 + X2//Xm) / (X1+Xm) * T''do