## EqCircut
.
What is the % BDT before Correlation ? |  |  |  | 191.5 |  |  | Voltage : |  | 4000 | First Cycle Inrush
What is the % BDT after Correlation ? |  |  |  | 262.5 |  |  | Frequency : |  | 60 | 2.3806
[7 empty] | No-Load Current: |  | 12.67 / 12.99
what are the No Load Amps? |  |  | 12.99 |  |  |  | Full Load Current: |  | 62.95 / 65.49
[7 empty] | Breakdown Torque: |  | 191.5 / 262.5
What are the Full load Amps? |  |  | 65.49 |  |  |  | Wc: |  | 7984.1 / 2779.8
[7 empty] | Wf: |  | 6000.0 / 5171.6
TOSHIBA INTERNATIONAL CORPORATION
ALL VALUES ARE IN EQULIVALENT Y
|  |  | VALUE (OHMS) |  | PER UNIT
BASE IMPEDANCE PER UNIT |  |  | 35.2634 |  | 1
PRIMARY REISTANCE (R1) |  |  | 0.21117 |  | 0.0059883
SECONDARY RESISTANCE (R2) |  |  | 0.21179 |  | 0.0060058 |  |  | Project or Lab:
STARTING RESISTANCE (R3) |  |  | 1.4362 |  | 0.040729 |  |  | RF2500
PRIMARY REACTANCE (X1) |  |  | 2.0469 |  | 0.058045
SECONDARY REACTANCE (X2) |  |  | 5.4737 |  | 0.15522
STARTING REACTANCE (X3) |  |  | 4.2589 |  | 0.12077
MAGNETIZING REACTANCE (XM) |  |  | 177.783 |  | 5.0416
TRANSIENT REACTANCE (Xd') |  |  | 7.3571 |  | 0.20863
SUB TRANSIENT REACTANCE (Xd") |  |  | 4.4103 |  | 0.12507
SHORT CIRCUIT TIME CONSTANT |  |  | 0.093902 |  | 0.0026629
SUB TRANSIENT TIME CONSTANT |  |  | 0.010594 |  | 0.00030043
OPEN CIRCUIT TIME CONSTANT |  |  | 2.2953 |  | 0.065089
INDUCTANCES (HENRIES)
STATOR INDUCTANCE (L1) |  |  | 0.0054295 |  | 0.00015397
ROTOR INDUCTANCE (L2) |  |  | 0.014519 |  | 0.00041174
STARTING INDUCTANCE (L3) |  |  | 0.011297 |  | 0.00032036
Rev.1 Added Starting Reactance. 11/18/04 MDC
Rev.2 Corrections to calculations & added first cycle inrush 1/28/09 JR & MDC
Rev.3 Corrected Calculation for R3 MDC 12/9/09
Rev.4 Correction to short circuit time constant. |  |  |  |  | Used to be "=(B57+((B56*B61)/(B56 * B61))/(B51*E41))" |  |  |  |  | Z.X 10/25/2019
Rev.5 Correction to short circuit time contstant. Used to be "=(B57+((B56*B61)/(B56+B61))/(B51*E41))" Z.X 12/14/2021
2*pi*f
| Jcon = | 1 | Wo = | 376.9911 | Xcorr = | .666666666666666666666666
| X BDT = | 1.3708
pacop = | 9.3817 |  | Xcorr * Coil End Reactance
pacop2= | 4.6908 |  | (1-Xcorr) * Coil End Reactance
pac11p = | 9.3817 |  | Xcorr * Coil End Reactance
pac12p = | 4.6908 |  | (1-Xcorr) * Coil End Reactance
base = | 35.2634 |  | Impedance (not used)
r1 = | 0.21117 |  | Primary Resistance
r2 = | 0.21179 |  | Seconadry Resistance
r3 = | 1.4362 |  | Starting Secondary Resistance
xs = | 7.5205 |  | Total Reactance
x1r = | 36.4672 |  | Stator Slot Reactance + 1/2 Zigzag Reactance + 1/2 Belt Leakage Reactance + Xcorr * Coil End Reactance
x2r = | 97.5192 |  | Rotor Slot Reactance + 1/2 Zigzag Reactance + 1/2 Belt Leakage Reactance + (1-Xcorr) * Coil End Reactance
x1 = | 2.0469 |  | Primary Reactance
x2 = | 5.4737 |  | Secondary Reactance
x1s = | 32.4783 |  | [Starting Stator Slot Reactance + 1/2 Starting Zigzag Reactance + Xcorr * Coil End Reactance] / Jconn
x2s = | 50.5625 |  | [Starting Rotor Slot Reactance + 1/2 Starting Zigzag Reactance + (1-Xcorr) * Coil End Reactance] / Jconn
x3 = | 4.2589 |  | Starting Rotor Reactance
xm= | 177.783 |  | Magnetizing Reactance
tx = | 7.3571 |  | Transient Reactance = Primary Reactance + Secondary Reactance // Magnetizing Reactance
stx = | 4.4103 |  | Sub Transient Reactance = Primary Reactance + Secondary Reactance // Magnetizing Reactance // Starting Secondary Reactance | [7 empty] | ???
sctc = | 0.093902 |  | Short circuit time constant = (X2 + X1//Xm) / (2*pi*f * r2)
sttc = | 0.010594 |  | sub transient time constant = (X3 + X1//X2//Xm) / (2*pi*f * r3)
octo = | 2.2953 |  | open circuit time constant = (Xm + X2) / (2*pi*f * r2)
l1 = | 0.0054295 |  | Primary Inductance
l2 = | 0.014519 |  | Secondary Inductance
l3 = | 0.011297 |  | Starting Rotor Inductance
NEMA MG1 way of short circuit AC time constant
sctc = | 0.093902 |  | Short circuit time constant = (X1 + X2//Xm) / (X1+Xm) * T''do