## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RAT FILES\1M2700U Rev.1.rat |  |  |  |  | Date: | 2022-06-27 | Time: | 13:28
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 700 | 3600 | FCKNW | 4000 | 60 | 105 | 3570.6 / 3571.1 | 0.0082 / 0.0080 | 5811/12USS
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.5437 | LR Test Data
Air Gap | 3.3 | [5 empty] | Rt. Slot Pitch | 30.4569 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 16 | Cross Section Area |  | Mean Value | 27.5003 | 665.0001
Core Length | 375 | 375 |  |  | UB: 406.6 | UER: 3370.3 | Eff.T.W.St. | 14.3389 | WS
OD | 670 | 368.4 | Coil Pitch | 0.62494 |  | ERT: 85.0 | Eff.T.W.Rt. | 30.4569 | 25887.6417
ID | 375 | 185 | Slot Fill | - |  | ERD1: 281.0 | St.Carter Fac. | 1.1789 | IS
Core Depth | 85 | 54.7 | Con./Slot | 16 |  | ERD2: 367.0 | Rt.Carter Fac. | 1 | 88.325
Eff.Core L. | 311.55 | 311.55 | Wire Size 1 | (.114"x.204")x2 |  |  | Carter Factor | 1.1789 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.83141 | 18.0427
Number | 48 | 38 | // Circuits | 1 |  |  | Distrib. Factor | 0.95544 | AC
Kind | Open | Dbl - Closed | Connection | Wye |  |  | Wind. Factor | 0.79436 | 575.7897
Skew | - | 0 | MCL | 1070 | 460 |  | Reactance | (Coeff.: 0.0566)
Depth | 62.5 | 37 | No.Cond./Ph. | 256 |  |  |  | Running | Start
Width | 10.20 - 10.20 |  | Res. (20°C) | 0.16506 |  |  | Stator Slot | 18.5331 | 18.5331
Opening | 14.5 | 0 | (105°C) | 0.22019 | 0.16096 | 0.075972 | Rotor Slot | 47.6104 | 20.9931
Tip Depth | 2.83 | 1.9 | Material | CU | AL | AL | Zigzag | 4.3345 | 4.1996
T.Min.Wid. | 10.0437 | 11 | Spec.Resist. | 1.742 | 3.25 | 3.25 | Coil End | 31.1087 | Skew R.: 0.00
Low. R. | 0 | 2 | Spec.Gravity | 8.89 | 2.67 | 2.67 | Belt Leakage | 7.2923 | 7.1049
Up. R. | - | 2 | Weight (kg) |  |  |  | Total Resist. | 0.45712 | 1.1061
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 211.1926 | 15.4685 | 18.6298 | Total React. | 6.1619 | 4.635
Duct | 4 x 10 | 4 x 10 | Wire 2 | - | - | - | Impedance | 6.1788 | 4.7652
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.0858 |  | Length | Section | Density | AT | Volume | Loss |  | 3563.4 | 125RPM |  | Kline/in2
| Reac.= | 35.0959 | Primary Core | 52.6216 | 529.635 | 16.098 | 644.0854 | 48668.9567 | 3734.1026 |  | 3571.1 | 100RPM |  | 103.8578
Excitation Data |  |  | Tooth | 6.25 | 750.9854 | 11.3532 | 21.8468 | 9387.3173 | 409.0674 |  | 3578.5 | 75RPM |  | 73.2461
Excit.Amps | 21.251 / 21.466 |  | Second.Core | 23.1221 | 532.9582 | 15.9976 | 275.5888 | Total | 4143.1701 |  | 3585.8 | 50RPM |  | 103.2102
Core Loss | 1.157 / 1.169 | Flux / Pole | Tooth | 3.7 | 651.1395 | 13.0941 | 19.5226 | C.L.C. | 1.75 / 0.85 |  | 3592.9 | 25RPM |  | 84.4777
NoLoad | 21.28 / 21.50 | 8.5261 | Air Gap | 0.33 | 1673.8348 | 5.0937 | 1337.6432 | S.F.C. | 6.05 |  |  |  |  | 32.8627
Load Characteristics |  |  | Temp. Rise @ 100%: | 58 / 56 |  | No Load Loss | 18247.0 / 16104.2 | W.Loss | 7250.5 / 3539.3
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 5153.2 / 5344.8 | S.Loss | 772.8 / 377.2
Current (A) | 32.43 / 32.63 | 48.91 / 49.20 | 67.94 / 68.36 | 88.32 / 88.86 | 109.82 / 110.48 | Second. Loss | 4508.2 / 4349.0 | Total C.Loss | 8023.3 / 3916.6
Efficiency | 0.873 / 0.864 | 0.927 / 0.917 | 0.944 / 0.933 | 0.950 / 0.940 | 0.953 / 0.942 | Frict.& Wind. | 10000.0 / 13436.0 | Stray Loss | 6306.2969 | 0.950 | 0.940 | 0.98947 | Eff.
P.F. | 0.665 / 0.669 | 0.831 / 0.836 | 0.882 / 0.886 | 0.898 / 0.902 | 0.900 / 0.905 | Starting Data |  | Slip | PF | 0.898 | 0.902 | 1.0045 | PF.
Slip | 0.0021 / 0.0020 | 0.0041 / 0.0039 | 0.0061 / 0.0060 | 0.0082 / 0.0080 | 0.0103 / 0.0102 | LRA | 484.7 / 618.1 |  |  | 88.32 | 88.86 | 1.0061 | Current
RPM | 3592.4 / 3592.9 | 3585.3 / 3585.8 | 3578.0 / 3578.5 | 3570.6 / 3571.1 | 3563.0 / 3563.4 | % | 548.7 / 699.8 |  |  | 3570.6 | 3571.1 | 1.0001 | RPM
L (Inv., MH) | 13.795 | 11.7034 | 10.6736 | 10.0644 | 9.668 | LRT (kg.m) | 169.3 / 179.7 |  | 0.23213
(No Load) | 22.7982 |  | Correlated to: TEFC-1250HP.dat |  |  | % | 118.8 / 126.1
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1182.7853 | 0.038427 | 0.63077
IM/IW | 0.26684 | I*R1/E | 0.0083678 | Rosenberg | 227.5549 | % | 224.6 / 230.6
IW*X/E | 0.21248 | I*R2/E | 0.0081704 | Schwisky | 428.1856 | Amps | 260.2477 |  |  | HP0.95 | 504.4791
SUM | 0.47933 | Friction/OP. | 0.01915 | Tsurumi | 184.1922 | Max. Output | 1138.2369 | 0.03693 | 0.64418 | HP1.5 | 18520.2598
IH/I | 0.013181 | Total | 0.048869 | Thrust (1mm) | 39.5166 | % | 217.9695 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.95113 | Thrust (3 mm) | 99.4953 | Amps | 255.031 |  |  | (RPM/1000)1.8 | 10.031
Double Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 38 | Slit Width | 6 | T.M.Wid.Low. | 11 | Watt Rad. | 0.063644 | Coil Cur. Density |  | k | 0.0685
Depth | 37 | Slit Depth | 9.1 | Cal.T.W.Up. | 0 | DG2L(cm2) | 45465.7176 | 3.06 / 3.07 |  | Hz | 60
Opening | 0 | L.S.Up.Wid. | 17.0029 | Cal.M.T.Wid. | 0 | GD2L(kg.m2) | 24.6822 | Bar Cur. Den. |  | Load Inertia | 503.1518
Tip Depth | 1.9 | L.S.Low.Wid. | 13.357 | Cal.M.T.Wid. | 11 | DO2L(cm2) | 150381.5 | UB: 3.14 / 3.16 | LB: - | 1/2 NEMA | 251.5759
Up. Sl. Wid. | 6 | L.S.Depth | 22 | X2S | 0 | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | 2 | T.M.Wid.Up. | 23.4813 | X3S | 0 | Coil Pitch Ct. | 0.68741 | UER: 2.30 / 2.31 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.23913 | 0.7 | 92.6092 | 680.4164
0.0076 | 86.8624 | 127.3554 | 0.8 | 97.9516 | 685.5839
0.038 | 230 | 447.2203 | 0.9 | 107.7891 | 690.2495
0.089091 | 170.3878 | 574.6872 | 1 | 125 | 694.382
0.14018 | 127.6008 | 615.6392
0.19127 | 107.3246 | 633.6266 | Acceleration Data (FV V)
0.29345 | 94.6778 | 650.7569 | Load Type: | Fan / Pump
0.39564 | 90.9787 | 660.5349 | Load Inertia: | 42.5 kg.m²
0.49782 | 90.0577 | 668.1199 | Accel. Time: | 5.8 (s)
0.6 | 90 | 674.7291 | Rated Torque: | 142.4 kg.m
92.697
Load
100
98.48
90.3
76.8364
63.5527
51.92
34.1127
22.48
14.1745
8
6
8
15
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | 1M2700U Rev.1 | [5 empty] | HRW / Model Number: | 7003TCQL11F-A
Type: TIKK - Form: FCKNW - 2 Pole - 700 HP - 4000 V - 60 Hz - 5811/12USS - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 3.3 |  | No load amps |  |  |  | 22 | 19.4 |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 375 |  | No load watts |  |  |  | 16104 | 15690 |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 8 |  | Impedance amps |  | 3 | f | 153 | 125.5 |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.114"x.204")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 25888 | 50500 |  | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [6 empty] | Dry Kiln
Connection |  | 1 x Wye |  |  | Winding |  | 80/115 | 58 / 77 | -
MCL |  | 1070 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 10.1404 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 16 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 89
Coil grouping |  | - |  |  |  | RPM |  | 3570
Coil pitch (slot number) |  | 1 ~ 16 |  |  |  | CODE |  | G
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.1634 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 12 |  |  |  | Nom.Eff. (%): |  | - |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 307 / 2132 | 316 / 231
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 618 | -
[6 empty] | LRT (%) | 60 | 126 | -
[6 empty] | BDT (%) | 175 | 230 | -
[6 empty] | SLIP (%) |  | 0.8 | -
[5 empty] | IEEE-B | Eff. (%) |  | 94 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 90.2 | -
|  |  |  | Losses (Watts) |  | Primary |  | 5345 | -
[6 empty] | Secondary |  | 4349 | -
[6 empty] | Core |  | 3917 | -
[6 empty] | F & W |  | 13436 | -
[6 empty] | Stray |  | 6306 | -
End Ring (Reference) |  |  |  | Note | 7003TCQL11F-A |  |  |  |  | 4160V REFER TO H050392
|  |  |  | LINK: | TEFC-1250HP.rat with TEFC-1250HP.dat
Run 1M2700U Rev.1.rat
F & W Loss for Sleeve Bearing : 13500W
Efficiency for Sleeve Bearing : 94.0 %
ODE Silencer w/ Cab-Foam
Approved |  | Design | W.McDaniel |  | DE Silencer w/ Cab-Foam
Date |  | Date | 2006-03-06 |  | Rev. 1 MCL changed from 1090 to 1070 mm.
A. Gracia (5/24/04)
Rev.2 Lead AWG changed from 04 to 02.
W.McDaniel (3/3/06)
REV.3 CHG MCL FROM 1090 & WIRE FROM
.114"x.204";.114"x.229" JR 08/06/09
62.5
2.83
14.5
3370.3
367.0
43.0
85.0
281.0
1.90
37.00
2.0
11.1
6.0
17.00
22.00
13.36
Section
mm2
Section
mm2
M
M
311-
411-
350-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 2 Pole - 700.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 252.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~360 | 116.4 | 22.5 | 0.482 | 616.2 | 121.6 | 367.6
360~720 | 102.9 | 11.5 | 0.495 | 612.2 | 123.4 | 293.1
720~1080 | 95.3 | 7.0 | 0.513 | 607.9 | 126.1 | 245.1
1080~1440 | 91.3 | 7.0 | 0.537 | 603.0 | 130.1 | 212.4
1440~1808 | 90.0 | 11.1 | 0.586 | 597.6 | 139.6 | 189.0
1808~2176 | 90.5 | 18.3 | 0.641 | 591.3 | 149.6 | 171.5
2176~2544 | 92.8 | 28.3 | 0.717 | 583.5 | 163.7 | 154.1
2544~2911 | 101.0 | 43.0 | 0.797 | 571.6 | 176.7 | 132.3
2911~3095 | 117.5 | 57.7 | 0.387 | 555.9 | 81.4 | 95.0
3095~3279 | 149.0 | 70.2 | 0.293 | 529.7 | 58.2 | 62.7
3279~3463 | 200.2 | 83.6 | 0.198 | 454.7 | 34.3 | 36.0
3463~3571 | 165.0 | 94.4 | 0.191 | 255.7 | 1.0 | 7.4
Acceleration Time: 5.8 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 1306 kW / s |  | 16°C |  | 32°C
Rotor Bar Rise | 1336 kW / s |  | 96°C |  | 193°C
End Ring Rise | 630 kW / s |  | 38°C |  | 76°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 3.5°C / s |  | 284.4 kW | 160°C | 45.8 s
Rotor Bar | 32.0°C / s |  | 443.5 kW | 260°C | 8.1 s
Rotor ER | 12.5°C / s |  | 209.3 kW | 180°C | 14.3 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 58°C + |  | 102°C + | 40°C | = 200°C | 29.2 s
Rotor Bar | 75°C + |  | 185°C + | 40°C | = 300°C | 5.8 s
Rotor ER | 75°C + |  | 105°C + | 40°C | = 220°C | 8.3 s
Cold Stall Time: | 7.0 s |  | Hot Stall Time: |  | 4.1 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | -
| TIC SR No.: | -
MOTOR NAMEPLATE DATA
| H.P.: | 700 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812USS |  | ENCL: | TEFC |  | FLAMPS: | 89 |  |  | FLRPM: | 3570
| FORM: | FCNW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKK |  | AMB.: | 40°C |  | CODE: | G |  |  | DUTY: | Cont.
| MODEL No.: | 7003TCQL11F-A |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 618 |  |  | FULL LOAD (lb-ft.): | 1030 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 125 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 230
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 94 | [5 empty] | FULL LOAD: | 90.2
|  | 3/4 LOAD: | 93.3 | [5 empty] | 3/4 LOAD: | 88.6
|  | 1/2 LOAD: | 91.7 | [5 empty] | 1/2 LOAD: | 83.6
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2022-06-27
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | 7003TCQL11F-A |  |  | FLAmps: | 89
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 146.4 lb-ft² | Date: | 2022-06-27
FLRPM: | 3570 | Load Inertia: | 252.0 lb-ft² | File: | 1M2700U
| Locked Rotor Amps: | 618 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 125% | Starting at: | FV (V)
| Breakdown Torque: | 230% | Accel. Time: | 5.8 (s)
| Rated Torque: | 1030 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | 1M2700U
|  | Prepared by: | Zichao Xie | Checked by:
Load
100 | 0 | 0.23913 | 100
99.24 | 86.8624 | 127.3554 | 98.48
96.2 | 230 | 447.2203 | 90.3
91.0909 | 170.3878 | 574.6872 | 76.8364
85.9818 | 127.6008 | 615.6392 | 63.5527
80.8727 | 107.3246 | 633.6266 | 51.92
70.6545 | 94.6778 | 650.7569 | 34.1127
60.4364 | 90.9787 | 660.5349 | 22.48
50.2182 | 90.0577 | 668.1199 | 14.1745
40 | 90 | 674.7291 | 8
30 | 92.6092 | 680.4164 | 6
20 | 97.9516 | 685.5839 | 8
10 | 107.7891 | 690.2495 | 15
0 | 125 | 694.382 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | 7003TCQL11F-A |  |  | FLAmps: | 89
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 146.4 lb-ft² | Date: | 2022-06-27
FLRPM: | 3570 | Load Inertia: | 252.0 lb-ft² | File: | 1M2700U
618 A
125%
1030 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | 1M2700U
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
694.382 | 10.0453 | 5.8319 |  | 694.382 | 0.0001
600 | 13.4541 | 7.8109 |  | 692.3596 | 0.482
500 | 19.3739 | 11.2477 |  | 687.8652 | 0.977
400 | 30.2718 | 17.5746 |  | 683.0337 | 1.49
300 | 53.8165 |  |  | 677.5281 | 2.027
200 | 121.0872 |  |  | 671.4607 | 2.613
230 | 91.5593 | 53.1557 |  | 664.382 | 3.254
180 | 200.22 | 86.7881 |  | 655.618 | 3.971
145 | 230.3679 | 133.7424 |  | 642.2472 | 4.768
125 |  | 300 |  | 624.6067 | 5.155
125 |  | 600 |  | 595.1685 | 5.448
125 |  | 10000 |  | 510.8989 | 5.646
|  |  |  | 125 | 5.837

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 7003TCQL11F-A |  |  | FLAmps: | 89
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 146.4 lb-ft² | Date: | 2022-06-27
FLRPM: | 3570 | Load Inertia: | 252.0 lb-ft² | File: | 1M2700U
| Locked Rotor Amps: | 618 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 125% | Starting at: | FV (V)
| Breakdown Torque: | 230% | Accel. Time: | 5.8 (s)
| Rated Torque: | 1030 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 3600 | 1400
[8 empty] | 3596 | 1260
Comments: | PROJECT | - |  | D.E.Curve #: | 1M2700U |  |  | 3592 | 1120
[8 empty] | 3588 | 980
[8 empty] | 3584 | 840
[8 empty] | 3580 | 700
|  | Prepared by: | Zichao Xie | Checked by: |  | SYNC SPEED | 3600 | 3576 | 560
[6 empty] | NEW SPEED LOWER RANGE | 3560 | 3572 | 420
[6 empty] | NEW kW UPPER RANGE | 1400 | 3568 | 280
[8 empty] | 3564 | 140
[8 empty] | 3560 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 22 | 100 | 1.1503
25 | 86.4 | 66.9 | 32.63 | 80.6122 | 10.8028
50 | 91.7 | 83.6 | 49.2 | 62.5 | 20.3547
75 | 93.3 | 88.6 | 68.36 | 43.8776 | 29.9729
100 | 94 | 90.2 | 88.86 | 25 | 39.6648
125 | 94.2 | 90.5 | 110.48 | 5.6122 | 49.4794
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 21.4122 | 100 | 18.4409
25 | 86.4013 | 66.8385 | 32.6286 | 81.8417 | 10.7921
50 | 91.7143 | 83.5092 | 49.2045 | 64.1286 | 20.3338
75 | 93.3875 | 88.5505 | 68.3578 | 45.9442 | 29.9543
100 | 94.0482 | 90.1843 | 88.8637 | 27.359 | 39.6584
125 | 94.2803 | 90.4442 | 110.4879 | 8.2736 | 49.451
3600
3596
3592
3588
3584
3580
3576
3572
3568
3564
3560
RPM
1400
700
560
420
280
140
Input Watts (kW)
840
980
1120
1260
EFF.
P.F.
RPM
AMPS
WATTS
0.0