## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RAT FILES\1M4800U_Rev1.rat |  |  |  |  | Date: | 2021-09-02 | Time: | 9:09
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
4 | 800 | 1800 | FCK | 4000 | 60 | 105 | 1780.3 / 1780.0 | 0.0109 / 0.0111 | 5811/12US
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 22.2529 | LR Test Data
Air Gap | 2.1 | [5 empty] | Rt. Slot Pitch | 30.045 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 14 | Cross Section Area |  | Mean Value | 26.149 | 499.2593
Core Length | 530 | 530 |  |  | UB: 400.9 | UER: 2750.0 | Eff.T.W.St. | 13.4603 | WS
OD | 670 | 420.8 | Coil Pitch | 0.86658 |  | ERT: 40.0 | Eff.T.W.Rt. | 30.045 | 24273.8531
ID | 425 | 220 | Slot Fill | - |  | ERD1: 280.0 | St.Carter Fac. | 1.2098 | IS
Core Depth | 65.5 | 67.6 | Con./Slot | 22 |  | ERD2: 420.0 | Rt.Carter Fac. | 1 | 98.3175
Eff.Core L. | 390.6 | 390.6 | Wire Size 1 | (.072"x.162")x1 |  |  | Carter Factor | 1.2098 | Volts / Turn
Slot Data |  |  | Wire Size 2 | (.072"x.182")x1 |  |  | Short. Factor | 0.97812 | 18.1818
Number | 60 | 44 | // Circuits | 1 |  |  | Distrib. Factor | 0.95651 | AC
Kind | Open | Dbl - Closed | Connection | Delta |  |  | Wind. Factor | 0.93558 | 561.2009
Skew | - | 0 | MCL | 1045 | 570 |  | Reactance | (Coeff.: 0.2195)
Depth | 57 | 32.8 | No.Cond./Ph. | 440 |  |  |  | Running | Start
Width | 8.79 - 8.79 |  | Res. (20°C) | 0.52142 |  |  | Stator Slot | 19.8625 | 19.8625
Opening | 12.7 | 0 | (105°C) | 0.69557 | 0.7158 | 0.12412 | Rotor Slot | 19.6879 | 8.574
Tip Depth | 2.83 | 0.8 | Material | CU | AL | AL | Zigzag | 7.2139 | 4.9951
T.Min.Wid. | 9.5529 | 14 | Spec.Resist. | 1.742 | 3.25 | 3.25 | Coil End | 13.3432 | Skew R.: 0.00
Low. R. | 0 | 2 | Spec.Gravity | 8.89 | 2.67 | 2.67 | Belt Leakage | 4.8766 | 3.4511
Up. R. | - | 2 | Weight (kg) |  |  |  | Total Resist. | 1.5355 | 2.511
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 88.4903 | 24.9628 | 17.8632 | Total React. | 14.2657 | 11.0096
Duct | 11 x 10 | 11 x 10 | Wire 2 | 99.8829 | - | - | Impedance | 14.3481 | 11.2923
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 31.9911 |  | Length | Section | Density | AT | Volume | Loss |  | 1775.0 | 125RPM |  | Kline/in2
| Reac.= | 31.9974 | Primary Core | 26.3108 | 511.686 | 14.2567 | 243.8418 | 48586.9186 | 3061.9346 |  | 1780.0 | 100RPM |  | 91.9788
Excitation Data |  |  | Tooth | 5.7 | 559.7061 | 13.0336 | 41.6705 | 12761.2994 | 695.4436 |  | 1785.1 | 75RPM |  | 84.0874
Excit.Amps | 13.514 / 13.268 |  | Second.Core | 13.9487 | 528.0912 | 13.8138 | 122.9474 | Total | 3757.3782 |  | 1790.0 | 50RPM |  | 89.1214
Core Loss | 0.563 / 0.553 | Flux / Pole | Tooth | 3.28 | 601.524 | 12.1275 | 19.0032 | C.L.C. | 1.50 / 0.75 |  | 1794.7 | 25RPM |  | 78.2417
NoLoad | 23.43 / 23.00 | 7.295 | Air Gap | 0.21 | 1158.7875 | 6.2953 | 1052.0337 | S.F.C. | 6.05 |  |  |  |  | 40.6151
Load Characteristics |  |  | Temp. Rise @ 100%: | 77 / 76 |  | No Load Loss | 11048.1 / 7611.2 | W.Loss | 5636.1 / 2833.7
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 6724.0 / 7666.1 | S.Loss | 1126.4 / 566.3
Current (A) | 34.76 / 35.85 | 53.45 / 55.12 | 75.15 / 77.50 | 98.32 / 101.40 | 122.72 / 126.57 | Second. Loss | 6816.9 / 7382.6 | Total C.Loss | 6762.4 / 3400.0
Efficiency | 0.926 / 0.914 | 0.955 / 0.942 | 0.961 / 0.948 | 0.962 / 0.949 | 0.960 / 0.947 | Frict.& Wind. | 4000.0 / 3990.0 | Stray Loss | 9566.3096 | 0.962 | 0.949 | 0.98649 | Eff.
P.F. | 0.669 / 0.657 | 0.844 / 0.829 | 0.894 / 0.879 | 0.911 / 0.895 | 0.914 / 0.898 | Starting Data |  | Slip | PF | 0.911 | 0.895 | 0.98244 | PF.
Slip | 0.0027 / 0.0029 | 0.0054 / 0.0056 | 0.0081 / 0.0083 | 0.0109 / 0.0111 | 0.0137 / 0.0139 | LRA | 613.5 / 729.3 |  |  | 98.32 | 101.40 | 1.0313 | Current
RPM | 1795.1 / 1794.7 | 1790.3 / 1790.0 | 1785.4 / 1785.1 | 1780.3 / 1780.0 | 1775.3 / 1775.0 | % | 624.0 / 741.8 |  |  | 1780.3 | 1780.0 | 0.99983 | RPM
L (Inv., MH) | 32.5184 | 29.277 | 27.6604 | 26.7158 | 26.0581 | LRT (kg.m) | 370.5 / 440.0 |  | 0.22237
(No Load) | 47.1699 |  | Correlated to: 1M4800U.dat |  |  | % | 113.5 / 134.8
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1526.0288 | 0.058807 | 0.61894
IM/IW | 0.25981 | I*R1/E | 0.0098469 | Rosenberg | 493.8742 | % | 252.9 / 294.2
IW*X/E | 0.1855 | I*R2/E | 0.010922 | Schwisky | 905.5685 | Amps | 334.9422 |  |  | HP0.95 | 572.7109
SUM | 0.44531 | Friction/OP. | 0.0067024 | Tsurumi | 759.1885 | Max. Output | 1439.0444 | 0.055302 | 0.64006 | HP1.5 | 22627.4163
IH/I | 0.0099419 | Total | 0.037413 | Thrust (1mm) | 153.793 | % | 241.1267 |  |  | (RPM/1000)2.4 | 4.0988
|  | Efficiency | 0.96259 | Thrust (3 mm) | 333.735 | Amps | 324.5135 |  |  | (RPM/1000)1.8 | 2.8807
Double Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 24
Slot Number | 44 | Slit Width | 12 | T.M.Wid.Low. | 14 | Watt Rad. | 0.075149 | Coil Cur. Density |  | k | 0.0685
Depth | 32.8 | Slit Depth | 3 | Cal.T.W.Up. | 0 | DG2L(cm2) | 74370.5089 | 3.70 / 3.81 |  | Hz | 60
Opening | 0 | L.S.Up.Wid. | 14.9447 | Cal.M.T.Wid. | 0 | GD2L(kg.m2) | 50.0421 | Bar Cur. Den. |  | Load Inertia | 2815.3914
Tip Depth | 0.8 | L.S.Low.Wid. | 11.3686 | Cal.M.T.Wid. | 14 | DO2L(cm2) | 188538 | UB: 3.64 / 3.76 | LB: -
Up. Sl. Wid. | 12 | L.S.Depth | 25 | X2S | 0 | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | 2 | T.M.Wid.Up. | 17.3596 | X3S | 0 | Coil Pitch Ct. | 0.89993 | UER: 1.87 / 1.92 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.23194 | 0.7 | 108.394 | 703.5504
0.005 | 78.5516 | 92.3607 | 0.8 | 112.5411 | 710.2915
0.025 | 271.042 | 365.2051 | 0.9 | 119.344 | 716.3395
0.05 | 290 | 528.7377 | 1 | 130 | 721.7822
0.10625 | 185.5615 | 596.3828
0.1625 | 148.2485 | 628.8784 | Acceleration Data (FV V)
0.275 | 120.7961 | 659.6067 | Load Type: | Fan / Pump
0.3875 | 109.6939 | 675.5302 | Load Inertia: | 474.6 kg.m²
0.5 | 105 | 686.7552 | Accel. Time: | 7.7 (s)
0.6 | 106.0782 | 695.9669 | Rated Torque: | 326.5 kg.m
Load
100
99
93.875
87
72.375
58.25
37.25
23.375
14
8
6
8
15
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | 1M4800U_Rev1 | [5 empty] | HRW / Model Number: | 8005TCAL11E-A
Type: TIKK - Form: FCK - 4 Pole - 800 HP - 4000 V - 60 Hz - 5811/12US - Class F | [9 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [5 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 2.1 |  | No load amps |  |  |  | 23 | - | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 530 |  | No load watts |  |  |  | 7611 | - | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 11 |  | Impedance amps |  | 3 | f | 226 | - | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.072"x.162")x1 |  | Impedance volts |  | 3 | f | 1150 | - | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | (.072"x.182")x1 |  | Impedance watts |  | 3 | f | 24274 | - | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [5 empty] | Dry Kiln
Connection |  | 1 x Delta |  |  | Winding |  | 80/115 | 77 / 102 | -
MCL |  | 1045 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 9.5364 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.5624 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 22 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 101
Coil grouping |  | - |  |  |  | RPM |  | 1780
Coil pitch (slot number) |  | 1 ~ 14 |  |  |  | CODE |  | H
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.5214 |  |  |  | DESIGN |  | - |  | Skip
Coil Weight | Wire1 | 194.7 |  |  |  | Nom.Eff. (%): |  | 94.5 |  | Adjacent
(lbs.) | Wire2 | 219.7 |  |  |  | Min.Eff. (%): |  | - |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | 89.5
FL / LR |  | 381 / 2750 | 376 / 192
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 729 | -
[6 empty] | LRT (%) | 60 | 134 | -
[6 empty] | BDT (%) | 175 | 294 | -
[6 empty] | SLIP (%) |  | 1.11 | -
[5 empty] | IEEE-B | Eff. (%) |  | 94.9 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 89.5 | -
|  |  |  | Losses (Watts) |  | Primary |  | 7666 | -
[6 empty] | Secondary |  | 7383 | -
[6 empty] | Core |  | 3400 | -
[6 empty] | F & W |  | 3990 | -
[6 empty] | Stray |  | 9566 | -
End Ring (Reference) |  |  |  | Note | Top-Hat TEAAC A/F Bearing
|  |  |  | LINK: | 1M4800U.rat with 1M4800U.dat
Run 1M4800U_Rev1.rat
Approved |  | Design | Matt.O |  | REV.1 UPDATE WIRE FROM (0.072"x 0.182") x 2
Date |  | Date | 2002-10-17 |  | Z.X 09/02/21
57.0
2.83
12.7
2750.0
420.0
70.0
40.0
280.0
0.80
32.80
2.0
5.0
12.0
14.94
25.00
11.37
Section
mm2
Section
mm2
M
M
311-
411-
350-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 4 Pole - 800.0 HP - 1800 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 2815.4 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~180 | 124.7 | 22.5 | 0.755 | 726.3 | 279.0 | 549.5
180~360 | 115.9 | 11.5 | 0.739 | 720.4 | 269.0 | 444.4
360~540 | 110.5 | 7.0 | 0.745 | 714.0 | 266.8 | 375.8
540~720 | 107.2 | 7.0 | 0.770 | 706.8 | 270.3 | 327.1
720~900 | 105.5 | 11.0 | 0.816 | 698.3 | 280.5 | 290.9
900~1103 | 107.3 | 18.7 | 0.978 | 688.0 | 327.4 | 255.7
1103~1305 | 115.2 | 30.3 | 1.022 | 674.2 | 330.9 | 216.3
1305~1508 | 134.5 | 47.8 | 1.000 | 650.7 | 308.6 | 165.3
1508~1609 | 166.9 | 65.3 | 0.427 | 618.8 | 119.8 | 102.4
1609~1710 | 237.8 | 79.7 | 0.274 | 568.2 | 69.3 | 53.9
1710~1755 | 280.5 | 90.4 | 0.101 | 451.4 | 20.1 | 32.9
1755~1780 | 185.5 | 96.4 | 0.122 | 231.1 | 0.9 | 14.4
Acceleration Time: 7.7 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2543 kW / s |  | 35°C |  | 70°C
Rotor Bar Rise | 2411 kW / s |  | 108°C |  | 216°C
End Ring Rise | 418 kW / s |  | 26°C |  | 52°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 6.1°C / s |  | 443.7 kW | 160°C | 26.2 s
Rotor Bar | 29.6°C / s |  | 661.2 kW | 260°C | 8.8 s
Rotor ER | 7.2°C / s |  | 114.7 kW | 180°C | 25.1 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 77°C + |  | 83°C + | 40°C | = 200°C | 13.6 s
Rotor Bar | 105°C + |  | 155°C + | 40°C | = 300°C | 5.3 s
Rotor ER | 105°C + |  | 75°C + | 40°C | = 220°C | 10.5 s
Cold Stall Time: | 10.4 s |  | Hot Stall Time: |  | 4.4 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | -
| TIC SR No.: | -
MOTOR NAMEPLATE DATA
| H.P.: | 800 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1800
| FRAME: | 5812US |  | ENCL: | TEAAC |  | FLAMPS: | 101 |  |  | FLRPM: | 1780
| FORM: | FCK1 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKK |  | AMB.: | 40°C |  | CODE: | H |  |  | DUTY: | Cont.
| MODEL No.: | 8005TCAL11E-A |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 729 |  |  | FULL LOAD (lb-ft.): | 2360 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 130 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 290
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 94.9 | [5 empty] | FULL LOAD: | 89.5
|  | 3/4 LOAD: | 94.8 | [5 empty] | 3/4 LOAD: | 87.9
|  | 1/2 LOAD: | 94.2 | [5 empty] | 1/2 LOAD: | 82.9
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2021-09-02
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | 8005TCAL11E-A |  |  | FLAmps: | 101
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 5812US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 800 | Rotor Inertia: | 296.9 lb-ft² | Date: | 2021-09-02
FLRPM: | 1780 | Load Inertia: | 2815.4 lb-ft² | File: | 1M4800U
| Locked Rotor Amps: | 729 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 130% | Starting at: | FV (V)
| Breakdown Torque: | 290% | Accel. Time: | 7.7 (s)
| Rated Torque: | 2360 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | 1M4800U
|  | Prepared by: | Zichao Xie | Checked by:
Load
100 | 0 | 0.23194 | 100
99.5 | 78.5516 | 92.3607 | 99
97.5 | 271.042 | 365.2051 | 93.875
95 | 290 | 528.7377 | 87
89.375 | 185.5615 | 596.3828 | 72.375
83.75 | 148.2485 | 628.8784 | 58.25
72.5 | 120.7961 | 659.6067 | 37.25
61.25 | 109.6939 | 675.5302 | 23.375
50 | 105 | 686.7552 | 14
40 | 106.0782 | 695.9669 | 8
30 | 108.394 | 703.5504 | 6
20 | 112.5411 | 710.2915 | 8
10 | 119.344 | 716.3395 | 15
0 | 130 | 721.7822 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | 8005TCAL11E-A |  |  | FLAmps: | 101
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 5812US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 800 | Rotor Inertia: | 296.9 lb-ft² | Date: | 2021-09-02
FLRPM: | 1780 | Load Inertia: | 2815.4 lb-ft² | File: | 1M4800U
729 A
130%
2360 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | 1M4800U
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
721.7822 | 14.8456 | 6.22 |  | 721.7822 | 0.0001
700 | 15.7839 | 6.6131 |  | 719.1089 | 0.755
600 | 21.4837 | 9.0012 |  | 713.2673 | 1.494
500 | 30.9365 | 12.9617 |  | 706.9307 | 2.239
400 | 48.3383 |  |  | 699.802 | 3.009
300 | 85.9347 |  |  | 691.3861 | 3.825
290 | 91.9634 | 38.5307 |  | 681.1881 | 4.803
180 | 253.7945 | 100.0134 |  | 667.5248 | 5.825
145 | 367.8536 | 154.1229 |  | 644.2574 | 6.825
125 |  | 400 |  | 612.6733 | 7.252
125 |  | 800 |  | 562.5743 | 7.526
125 |  | 10000 |  | 446.9307 | 7.627
|  |  |  | 227.9093 | 7.749

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 8005TCAL11E-A |  |  | FLAmps: | 101
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 5812US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 800 | Rotor Inertia: | 296.9 lb-ft² | Date: | 2021-09-02
FLRPM: | 1780 | Load Inertia: | 2815.4 lb-ft² | File: | 1M4800U
| Locked Rotor Amps: | 729 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 130% | Starting at: | FV (V)
| Breakdown Torque: | 290% | Accel. Time: | 7.7 (s)
| Rated Torque: | 2360 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 1800 | 1600
[8 empty] | 1797 | 1440
Comments: | PROJECT | - |  | D.E.Curve #: | 1M4800U |  |  | 1794 | 1280
[8 empty] | 1791 | 1120
[8 empty] | 1788 | 960
[8 empty] | 1785 | 800
|  | Prepared by: | Zichao Xie | Checked by: |  | SYNC SPEED | 1800 | 1782 | 640
[6 empty] | NEW SPEED LOWER RANGE | 1770 | 1779 | 480
[6 empty] | NEW kW UPPER RANGE | 1600 | 1776 | 320
[8 empty] | 1773 | 160
[8 empty] | 1770 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 23 | 100 | 0.47569
25 | 91.4 | 65.7 | 35.85 | 83.418 | 10.1989
50 | 94.2 | 82.9 | 55.12 | 67.1745 | 19.7863
75 | 94.8 | 87.9 | 77.5 | 50.592 | 29.4979
100 | 94.9 | 89.5 | 101.4 | 33.3333 | 39.2972
125 | 94.7 | 89.8 | 126.57 | 16.4128 | 49.2162
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 24.159 | 100 | 11.1934
25 | 91.3434 | 65.7269 | 35.8494 | 82.4898 | 10.2026
50 | 94.1697 | 82.929 | 55.1206 | 66.5178 | 19.7929
75 | 94.8192 | 87.8692 | 77.4979 | 50.2381 | 29.4859
100 | 94.8894 | 89.4805 | 101.3948 | 33.2828 | 39.2855
125 | 94.7221 | 89.7694 | 126.5587 | 16.5453 | 49.1936
1800
1797
1794
1791
1788
1785
1782
1779
1776
1773
1770
RPM
1600
800
640
480
320
160
Input Watts (kW)
960
1120
1280
1440
EFF.
P.F.
RPM
AMPS
WATTS
0.0