## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RATFILE\BS2700U.rat |  |  |  |  | Date: | 2018-03-27 | Time: | 8:19
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 700 | 3600 | FCKNW | 4160 | 60 | 105 | 3581.8 / 3577.3 | 0.0051 / 0.0063 | 5811/12UDZ
Core Data |  |  | Winding Data | USA Wire Std |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.5437 | LR Test Data
Air Gap | 3.3 | [5 empty] | Rt. Slot Pitch | 30.4569 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 16 | Cross Section Area |  | Mean Value | 27.5003 | 634.5475
Core Length | 375 | 375 |  |  | UB: 304.0 | UER: 1750.0 | Eff.T.W.St. | 14.3389 | WS
OD | 670 | 368.4 | Coil Pitch | 0.62494 |  |  | Eff.T.W.Rt. | 30.0388 | 20288.5461
ID | 375 | 185 | Slot Fill | - | EBL: 50.0 | ERD1: 281.0 | St.Carter Fac. | 1.1789 | IS
Core Depth | 85 | 55.29 | Con./Slot | 16 |  | ERT: 70.00 | Rt.Carter Fac. | 1.0139 | 84.0376
Eff.Core L. | 311.55 | 311.55 | Wire Size 1 | (.114"x.204")x2 |  | ERH: 25.00 | Carter Factor | 1.1953 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.83141 | 18.7644
Number | 48 | 38 | // Circuits | 1 |  |  | Distrib. Factor | 0.95544 | AC
Kind | Open | Trapeze | Connection | Wye |  |  | Wind. Factor | 0.79436 | 547.8403
Skew | - | 0 | MCL | 1070 | 545 |  | Reactance | (Coeff.: 0.0566)
Depth | 62.5 | 36.41 | No.Cond./Ph. | 256 |  |  |  | Running | Start
Width | 10.20 - 10.20 |  | Res. (20°C) | 0.16506 |  |  | Stator Slot | 18.5331 | 18.5331
Opening | 14.5 | 3 | (105°C) | 0.22019 | 0.13854 | 0.021607 | Rotor Slot | 16.8041 | 14.8054
Tip Depth | 2.83 | 3 | Material | CU | CU | CU | Zigzag | 4.1275 | 3.9029
T.Min.Wid. | 10.0437 | 10.3166 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 31.1087 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 7.1922 | 6.8009
Up. R. | - | 4.72 | Weight (kg) |  |  |  | Total Resist. | 0.38033 | 0.9576
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 211.1926 | 63.1588 | 26.4494 | Total React. | 4.4011 | 4.2531
Duct | 4 x 10 | 4 x 10 | Wire 2 | - | - | - | Impedance | 4.4175 | 4.3596
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 33.372 |  | Length | Section | Density | AT | Volume | Loss |  | 3572.8 | 125RPM
| Reac.= | 33.3991 | Primary Core | 52.6216 | 529.635 | 16.7419 | 760.1232 | 48668.9567 | 3979.0583 |  | 3577.3 | 100RPM
Excitation Data |  |  | Tooth | 6.25 | 750.9854 | 11.8073 | 24.4652 | 9387.3173 | 435.9021 |  | 3581.8 | 75RPM
Excit.Amps | 23.493 / 19.019 |  | Second.Core | 23.2148 | 536.6345 | 16.5235 | 317.3244 | Total | 4414.9604 |  | 3586.3 | 50RPM
Core Loss | 1.192 / 0.965 | Flux / Pole | Tooth | 3.641 | 610.6866 | 14.5199 | 28.761 | C.L.C. | 1.75 / 0.66 |  | 3590.7 | 25RPM
NoLoad | 23.52 / 19.04 | 8.8671 | Air Gap | 0.33 | 1650.8553 | 5.3712 | 1410.5134 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 62 / 64 |  | No Load Loss | 22372.5 / 14575.8 | W.Loss | 7726.2 / 2921.9
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 4665.1 / 5041.2 | S.Loss | 873.1 / 330.2
Current (A) | 33.27 / 34.08 | 47.96 / 49.12 | 65.38 / 66.97 | 84.04 / 86.08 | 103.55 / 106.07 | Second. Loss | 2757.4 / 3406.3 | Total C.Loss | 8599.2 / 3252.1
Efficiency | 0.850 / 0.847 | 0.915 / 0.911 | 0.937 / 0.933 | 0.947 / 0.943 | 0.952 / 0.948 | Frict.& Wind. | 13500.0 / 11229.4 | Stray Loss | 8622.9355 | 0.947 | 0.943 | 0.99578 | Eff.
P.F. | 0.641 / 0.628 | 0.826 / 0.809 | 0.887 / 0.870 | 0.911 / 0.893 | 0.919 / 0.901 | Starting Data |  | Slip | PF | 0.911 | 0.893 | 0.98024 | PF.
Slip | 0.0013 / 0.0026 | 0.0026 / 0.0038 | 0.0038 / 0.0050 | 0.0051 / 0.0063 | 0.0063 / 0.0076 | LRA | 550.9 / 522.9 |  |  | 84.04 | 86.08 | 1.0243 | Current
RPM | 3595.1 / 3590.7 | 3590.8 / 3586.3 | 3586.3 / 3581.8 | 3581.8 / 3577.3 | 3577.3 / 3572.8 | % | 655.6 / 622.3 |  |  | 3581.8 | 3575 | 0.9981 | RPM
L (Inv., MH) | 10.2162 | 10.2162 | 10.2162 | 10.2162 | 10.2162 | LRT (kg.m) | 182.0 / 112.0 |  | 0.21966
(No Load) | 10.2162 |  | Correlated to: LAB 8292.dat |  |  | % | 128.2 / 78.9
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1790.6327 | 0.036342 | 0.63668
IM/IW | 0.3101 | I*R1/E | 0.0076468 | Rosenberg | 253.023 | % | 341.2 / 270.2
IW*X/E | 0.13882 | I*R2/E | 0.0050512 | Schwisky | 469.5722 | Amps | 376.1337 |  |  | HP0.95 | 504.4791
SUM | 0.44892 | Friction/OP. | 0.025852 | Tsurumi | 199.2223 | Max. Output | 1726.7969 | 0.034984 | 0.64961 | HP1.5 | 18520.2592
IH/I | 0.014293 | Total | 0.052843 | Thrust (1mm) | 43.3361 | % | 330.6773 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.94716 | Thrust (3 mm) | 109.1121 | Amps | 368.9123 |  |  | (RPM/1000)1.8 | 10.031
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 38 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.057616 | Coil Cur. Density |  | k | 0.0685
Depth | 36.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 45465.7176 | 2.91 / 2.98 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 24.6822 | Bar Cur. Den. |  | Load Inertia | 503.1518
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 150381.5 | UB: 4.00 / 4.10 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.68741 | UER: 4.21 / 4.31 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.27352 | 0.69558 | 76.7616 | 601.1686
0.0072 | 146.344 | 161.4752 | 0.79705 | 75.8401 | 603.8129
0.036 | 270 | 474.0522 | 0.89853 | 75.3005 | 606.1207
0.086737 | 166.4063 | 551.4606 | 1 | 75 | 608.1395
0.13747 | 122.5545 | 571.4891
0.18821 | 102.8903 | 579.4815 | Acceleration Data (FV / 0.90 V)
0.28968 | 90.5973 | 586.6202 | Load Type: | Compressor
0.39116 | 84.4716 | 590.9969 | Load Inertia: | 84.8 kg.m²
0.49263 | 80.6918 | 594.7596 | Accel. Time: | 13.7 / 20.2 (s)
0.59411 | 78.2767 | 598.1526 | Rated Torque: | 142.0 kg.m
DesPro8AX Draft
Load | Torque 90% | LRA 90%
39 | 0 | 21.1707
37.56 | 118.5387 | 145.3277
36.35 | 218.7 | 426.6469
35.2653 | 134.7891 | 496.3145
34.2505 | 99.2691 | 514.3401
33.2358 | 83.3412 | 521.5333
32.1032 | 73.3838 | 527.9582
31.0884 | 68.422 | 531.8972
30.0737 | 65.3604 | 535.2836
30 | 63.4041 | 538.3373
30.9558 | 62.1769 | 541.0517
32.9411 | 61.4305 | 543.4316
34.9705 | 60.9934 | 545.5086
40 | 60.75 | 547.3256

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | BS2700U | [5 empty] | HRW / Model Number:
Type: TIKE - Form: FCKNW - 2 Pole - 700 HP - 4160 V - 60 Hz - 5811/12UDZ - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test |  |  |  |  | Q.C. 180400659 |  | EQP-III | M36 - 26Ga.
Air Gap |  | 3.3 |  | No load amps |  |  |  | 19 | 18.3 |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 375 |  | No load watts |  |  |  | 14576 | 12494 |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 8 |  | Impedance amps |  | 3 | f | 152 | 136 |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (061-0023-06) |  | (.114"x.204")x2 |  | Impedance volts |  | 3 | f | 1150 | 1150 |  | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 20289 | 48416 |  | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 1 x Wye |  |  | Winding |  | 80/115 | 62 / 82 | -
MCL |  | 1070 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 10.1404 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 16 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 86 |  | 559
Coil grouping |  | - |  |  |  | RPM |  | 3575
Coil pitch (slot number) |  | 1 ~ 16 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.1634 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 484 |  |  |  | Nom.Eff. (%): |  | - |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 298 / 1812 | 410 / 431
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 523 | - | 608.1395
[6 empty] | LRT (%) | 60 | 78 | -
[6 empty] | BDT (%) | 175 | 270 | -
[6 empty] | SLIP (%) |  | 0.63 | -
[5 empty] | IEEE-B | Eff. (%) |  | 94.3 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 89.3 | -
|  |  |  | Losses (Watts) |  | Primary |  | 5041 | -
[6 empty] | Secondary |  | 3406 | -
[6 empty] | Core |  | 3252 | -
[6 empty] | F & W |  | 11229 | -
[6 empty] | Stray |  | 8623 | -
End Ring (Reference) |  |  |  | Note | BASE BS2M70U
|  |  |  | LINK: | BS2800U.RAT & LAB 8292.DAT
WIPS 350-N129-01 (SAME AS 1M2700)
RSO2: 400-N158-06
TOP HAT: 135-N201-121USS GREATER THAN 85dBA BUT LESS THAN 90dBA
TOP HAT 135-N213-112316 FOR 85dBA
Approved |  | Design | Z. XIE
Date |  | Date | 2018-03-27 |  | REV.0 FIRST ISSUE
331.0
25.0
50.0
70.0
M
36.41
3.00
3.00
14.12
4.72
62.5
2.83
14.5
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 2 Pole - 700.0 HP - 3600 RPM - 4160 V - 60 Hz
Starting Performance
Load Type: Compressor - 503.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~365 | 60.9 | 37.5 | 3.209 | 469.9 | 469.7 | 1047.2
365~731 | 61.2 | 34.0 | 2.751 | 468.2 | 399.9 | 809.7
731~1096 | 61.8 | 31.9 | 2.512 | 466.3 | 362.4 | 660.5
1096~1461 | 62.8 | 30.5 | 2.325 | 464.1 | 332.5 | 540.1
1461~1827 | 64.4 | 30.0 | 2.189 | 461.7 | 310.0 | 443.0
1827~2192 | 66.9 | 30.6 | 2.069 | 458.9 | 289.6 | 357.8
2192~2557 | 70.9 | 31.6 | 1.911 | 455.7 | 264.1 | 274.7
2557~2922 | 78.4 | 32.7 | 1.643 | 451.3 | 223.8 | 187.6
2922~3105 | 91.3 | 33.7 | 0.652 | 445.4 | 86.6 | 109.8
3105~3288 | 117.0 | 34.8 | 0.456 | 434.6 | 59.0 | 66.9
3288~3470 | 176.7 | 35.8 | 0.266 | 396.9 | 32.1 | 33.5
3470~3574 | 168.6 | 37.0 | 0.162 | 245.9 | 14.4 | 24.1
3574~3582 | 109.3 | 38.3 | 0.022 | 71.6 | 0.1 | 3.4
Acceleration Time: 20.2 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2844 kW / s |  | 35°C |  | 70°C
Rotor Bar Rise | 3943 kW / s |  | 162°C |  | 324°C
End Ring Rise | 615 kW / s |  | 60°C |  | 121°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 2.5°C / s |  | 206.4 kW | 160°C | 63.0 s
Rotor Bar | 13.9°C / s |  | 338.8 kW | 260°C | 18.7 s
Rotor ER | 5.2°C / s |  | 52.8 kW | 180°C | 34.7 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 62°C + |  | 98°C + | 40°C | = 200°C | 38.6 s
Rotor Bar | 82°C + |  | 178°C + | 40°C | = 300°C | 12.8 s
Rotor ER | 82°C + |  | 98°C + | 40°C | = 220°C | 19.0 s
Cold Stall Time: | 25.9 s |  | Hot Stall Time: |  | 14.2 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | FS ELLIOTT CO LLC
| TIC SR No.: | 2079542.1
MOTOR NAMEPLATE DATA
| H.P.: | 700 |  | VOLTS: | 4160 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812USS |  | ENCL: | TEAAC |  | FLAMPS: | 86 |  |  | FLRPM: | 3575
| FORM: | FCKNW |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | TW-10009426 |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 523 |  |  | FULL LOAD (lb-ft.): | 1028 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 75 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 270
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 94.3 | [5 empty] | FULL LOAD: | 89.3
|  | 3/4 LOAD: | 93.3 | [5 empty] | 3/4 LOAD: | 87
|  | 1/2 LOAD: | 91.1 | [5 empty] | 1/2 LOAD: | 80.9
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2018-03-27
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | TW-10009426 |  |  | FLAmps: | 86
Enclosure: | TEAAC | Voltage: | 4160 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 146.4 lb-ft² | Date: | 2018-03-27
FLRPM: | 3575 | Load Inertia: | 503.0 lb-ft² | File: | BS2700U_4160V
| Locked Rotor Amps: | 523 A | Load Type: | Compressor
| Locked Rotor Torque: | 75% | Starting at: | FV / 0.90 (V)
| Breakdown Torque: | 270% | Accel. Time: | 13.7 / 20.2 (s)
| Rated Torque: | 1028 lb-ft
Comments: | PROJECT | 2079542.1 |  | D.E.Curve #: | BS2700U_4160V
|  | Prepared by: | Zichao Xie | Checked by:
|  |  | Load | Torque 90% | LRA 90%
100 | 0 | 0.27352 | 39 | 0 | 21.1707
99.28 | 146.344 | 161.4752 | 37.56 | 118.5387 | 145.3277
96.4 | 270 | 474.0522 | 36.35 | 218.7 | 426.6469
91.3263 | 166.4063 | 551.4606 | 35.2653 | 134.7891 | 496.3145
86.2526 | 122.5545 | 571.4891 | 34.2505 | 99.2691 | 514.3401
81.1789 | 102.8903 | 579.4815 | 33.2358 | 83.3412 | 521.5333
71.0316 | 90.5973 | 586.6202 | 32.1032 | 73.3838 | 527.9582
60.8842 | 84.4716 | 590.9969 | 31.0884 | 68.422 | 531.8972
50.7368 | 80.6918 | 594.7596 | 30.0737 | 65.3604 | 535.2836
40.5895 | 78.2767 | 598.1526 | 30 | 63.4041 | 538.3373
30.4421 | 76.7616 | 601.1686 | 30.9558 | 62.1769 | 541.0517
20.2947 | 75.8401 | 603.8129 | 32.9411 | 61.4305 | 543.4316
10.1474 | 75.3005 | 606.1207 | 34.9705 | 60.9934 | 545.5086
0 | 75 | 608.1395 | 40 | 60.75 | 547.3256

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | TW-10009426 |  |  | FLAmps: | 86
Enclosure: | TEAAC | Voltage: | 4160 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 146.4 lb-ft² | Date: | 2018-03-27
FLRPM: | 3575 | Load Inertia: | 503.0 lb-ft² | File: | BS2700U_4160V
523 A
75%
1028 lb-ft
Comments: | PROJECT | 2079542.1 |  | D.E.Curve #: | BS2700U_4160V
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
608.1395 | 35 | 15 |  | 608.1395 | 0.0001
543.4328 | 43.8311 | 18.7848 |  | 607.093 | 1.992
478.7067 | 56.4853 | 24.208 |  | 605 | 3.797
414 | 75.5221 | 32.3666 |  | 602.4419 | 5.488
314 | 131.285 |  |  | 599.6512 | 7.086
214 | 282.6487 |  |  | 596.5116 | 8.606
270 | 177.5608 | 76.0975 |  | 592.907 | 10.05
180 | 500.3158 | 171.2193 |  | 588.8372 | 11.393
145 | 615.6566 | 263.8528 |  | 583.0233 | 12.565
125 |  | 600 |  | 575.4651 | 13.04
125 |  | 1200 |  | 561.5116 | 13.382
125 |  | 10000 |  | 512.7907 | 13.588
|  |  |  | 270 | 13.712
|  |  |  | 125 | 13.731

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | TW-10009426 |  |  | FLAmps: | 86
Enclosure: | TEAAC | Voltage: | 4160 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 146.4 lb-ft² | Date: | 2018-03-27
FLRPM: | 3575 | Load Inertia: | 503.0 lb-ft² | File: | BS2700U_4160V
| Locked Rotor Amps: | 523 A | Load Type: | Compressor
| Locked Rotor Torque: | 75% | Starting at: | FV / 0.90 (V)
| Breakdown Torque: | 270% | Accel. Time: | 13.7 / 20.2 (s)
| Rated Torque: | 1028 lb-ft
Comments: | PROJECT | 2079542.1 |  | D.E.Curve #: | BS2700U_4160V
|  | Prepared by: | Zichao Xie | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 24.0947 | 100 | 1.0411
25 | 84.6527 | 62.7957 | 34.0761 | 70.7767 | 11.0127
50 | 91.1076 | 80.9484 | 49.1232 | 59.8576 | 20.4649
75 | 93.2976 | 86.9822 | 66.9638 | 48.7695 | 29.9767
100 | 94.2856 | 89.2758 | 86.0797 | 37.5252 | 39.5501
125 | 94.7649 | 90.1113 | 106.0627 | 26.1469 | 49.1876
3600
3596
3592
3588
3584
3580
3576
3572
3568
3564
3560
RPM
1400
700
560
420
280
140
Input Watts (kW)
840
980
1120
1260
EFF.
P.F.
RPM
AMPS
WATTS
0