## DesignSheet 80%V
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RAT FILES\BS2M20U.rat |  |  |  |  | Date: | 2024-08-08 | Time: | 13:23
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 1000 | 3600 | FCKNW | 3200 | 60 | 105 | 3569.1 / 3568.5 | 0.0086 / 0.0088 | 5811/12UDZ
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.5437 | LR Test Data
Air Gap | 3.3 | [5 empty] | Rt. Slot Pitch | 30.4569 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 16 | Cross Section Area |  | Mean Value | 27.5003 | 770.4198
Core Length | 510 | 510 |  |  | UB: 304.0 | UER: 1750.0 | Eff.T.W.St. | 14.3389 | WS
OD | 670 | 368.4 | Coil Pitch | 0.62494 |  |  | Eff.T.W.Rt. | 30.0388 | 45278.502
ID | 375 | 185 | Slot Fill | - | EBL: 50.0 | ERD1: 281.0 | St.Carter Fac. | 1.1789 | IS
Core Depth | 85 | 55.29 | Con./Slot | 24 |  | ERT: 70.00 | Rt.Carter Fac. | 1.0139 | 150.8125
Eff.Core L. | 409.2 | 409.2 | Wire Size 1 | (.072"x.204")x2 |  | ERH: 25.00 | Carter Factor | 1.1953 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.83141 | 19.2456
Number | 48 | 38 | // Circuits | 2 |  |  | Distrib. Factor | 0.95544 | AC
Kind | Open | Trapeze | Connection | Wye |  |  | Wind. Factor | 0.79436 | 737.3593
Skew | - | 0 | MCL | 1225 | 680 |  | Reactance | (Coeff.: 0.0418)
Depth | 62.5 | 36.41 | No.Cond./Ph. | 192 |  |  |  | Running | Start
Width | 10.20 - 10.20 |  | Res. (20°C) | 0.11174 |  |  | Stator Slot | 18.5331 | 18.5331
Opening | 14.5 | 3 | (105°C) | 0.14905 | 0.097229 | 0.012154 | Rotor Slot | 16.8041 | 14.8054
Tip Depth | 2.83 | 3 | Material | CU | CU | CU | Zigzag | 4.1275 | 4.0209
T.Min.Wid. | 10.0437 | 10.3166 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 24.3666 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 7.1922 | 7.0065
Up. R. | - | 4.72 | Weight (kg) |  |  |  | Total Resist. | 0.25844 | 0.66358
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 230.0125 | 77.023 | 26.4494 | Total React. | 2.9696 | 2.8738
Duct | 7 x 10 | 7 x 10 | Wire 2 | - | - | - | Impedance | 2.9809 | 2.9495
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 33.372 |  | Length | Section | Density | AT | Volume | Loss |  | 3560.5 | 125RPM |  | Kline/in2
| Reac.= | 33.3991 | Primary Core | 52.6216 | 695.64 | 13.0735 | 276.137 | 63923.4102 | 3500.9017 |  | 3568.5 | 100RPM |  | 84.3451
Excitation Data |  |  | Tooth | 6.25 | 986.3689 | 9.2201 | 11.7039 | 12329.6116 | 383.5205 |  | 3576.6 | 75RPM |  | 59.4847
Excit.Amps | 18.717 / 15.626 |  | Second.Core | 23.2148 | 704.8334 | 12.903 | 116.5058 | Total | 3884.4221 |  | 3584.3 | 50RPM |  | 83.245
Core Loss | 1.342 / 1.121 | Flux / Pole | Tooth | 3.641 | 802.0958 | 11.3384 | 12.679 | C.L.C. | 1.75 / 0.85 |  | 3591.6 | 25RPM |  | 73.1507
NoLoad | 18.77 / 15.67 | 9.0945 | Air Gap | 0.33 | 2168.2876 | 4.1943 | 1101.4498 | S.F.C. | 6.05 |  |  |  |  | 27.06
Load Characteristics |  |  | Temp. Rise @ 100%: | 107 / 83 |  | No Load Loss | 21064.4 / 18511.9 | W.Loss | 6797.7 / 3283.3
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 10170.5 / 9867.8 | S.Loss | 649.2 / 313.6
Current (A) | 43.42 / 44.06 | 76.87 / 78.00 | 112.78 / 114.43 | 150.81 / 153.03 | 191.25 / 194.05 | Second. Loss | 6875.4 / 7142.0 | Total C.Loss | 7447.0 / 3596.9
Efficiency | 0.894 / 0.887 | 0.937 / 0.929 | 0.949 / 0.942 | 0.952 / 0.945 | 0.952 / 0.945 | Frict.& Wind. | 13500.0 / 17822.6 | Stray Loss | 5148.9902 | 0.952 | 0.945 | 0.99265 | Eff.
P.F. | 0.867 / 0.861 | 0.934 / 0.928 | 0.943 / 0.937 | 0.937 / 0.931 | 0.924 / 0.918 | Starting Data |  | Slip | PF | 0.937 | 0.931 | 0.9936 | PF.
Slip | 0.0022 / 0.0023 | 0.0042 / 0.0044 | 0.0063 / 0.0065 | 0.0086 / 0.0088 | 0.0108 / 0.0110 | LRA | 626.4 / 605.4 |  |  | 150.81 | 153.03 | 1.0147 | Current
RPM | 3592.3 / 3591.6 | 3584.9 / 3584.3 | 3577.3 / 3576.6 | 3569.1 / 3568.5 | 3561.2 / 3560.5 | % | 415.4 / 401.4 |  |  | 3569.1 | 3568.5 | 0.99983 | RPM
L (Inv., MH) | 6.8955 | 6.8955 | 6.8955 | 6.8955 | 6.8955 | LRT (kg.m) | 164.2 / 116.1 |  | 0.22499
(No Load) | 6.8955 |  | Correlated to: lab 1125 1126.dat |  |  | % | 80.7 / 57.1
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1590.8846 | 0.036787 | 0.64479
IM/IW | 0.12931 | I*R1/E | 0.012251 | Rosenberg | 202.6483 | % | 211.4 / 141.3
IW*X/E | 0.23266 | I*R2/E | 0.0085696 | Schwisky | 376.0843 | Amps | 428.7624 |  |  | HP0.95 | 707.9458
SUM | 0.36197 | Friction/OP. | 0.018097 | Tsurumi | 159.5589 | Max. Output | 1533.4879 | 0.035396 | 0.65806 | HP1.5 | 31622.7766
IH/I | 0.0088391 | Total | 0.047756 | Thrust (1mm) | 42.2753 | % | 205.5614 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.95224 | Thrust (3 mm) | 106.3375 | Amps | 420.4279 |  |  | (RPM/1000)1.8 | 10.031
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 38 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.10972 | Coil Cur. Density |  | k | 0.0685
Depth | 36.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 59716.1664 | 4.11 / 4.17 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 32.4184 | Bar Cur. Den. |  | Load Inertia | 667.617
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 197516 | UB: 5.73 / 5.82 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.68741 | UER: 6.03 / 6.12 | LER: -
S-T Curve Data
Slip | Torque (%) | Amps | Slip | Torque (%) | Amps
0 | 0 | 0 | 0.7 | 90.8803 | 637.1064
0.01 | 114.4417 | 168.8147 | 0.8 | 87.3202 | 640.1135
0.05 | 213.1272 | 500.2984 | 0.9 | 84.08 | 642.7438
0.1 | 160.272 | 583.0142 | 1 | 81.1618 | 645.0492
0.15 | 132.0742 | 604.4728
0.2 | 118.7347 | 613.0556
0.3 | 107.9247 | 620.7941
0.4 | 102.8704 | 625.6357
0.5 | 98.7186 | 629.8548
0.6 | 94.7126 | 633.6864

## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RAT FILES\BS2M20U.rat |  |  |  |  | Date: | 2024-08-08 | Time: | 11:59
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 1000 | 3600 | FCKNW | 4000 | 60 | 105 | 3581.0 / 3580.3 | 0.0053 / 0.0055 | 5811/12UDZ
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.5437 | LR Test Data
Air Gap | 3.3 | [5 empty] | Rt. Slot Pitch | 30.4569 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 16 | Cross Section Area |  | Mean Value | 27.5003 | 618.664
Core Length | 510 | 510 |  |  | UB: 304.0 | UER: 1750.0 | Eff.T.W.St. | 14.3389 | WS
OD | 670 | 368.4 | Coil Pitch | 0.62494 |  |  | Eff.T.W.Rt. | 30.0388 | 29591.7483
ID | 375 | 185 | Slot Fill | - | EBL: 50.0 | ERD1: 281.0 | St.Carter Fac. | 1.1789 | IS
Core Depth | 85 | 55.29 | Con./Slot | 24 |  | ERT: 70.00 | Rt.Carter Fac. | 1.0139 | 121.9205
Eff.Core L. | 409.2 | 409.2 | Wire Size 1 | (.072"x.204")x2 |  | ERH: 25.00 | Carter Factor | 1.1953 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.83141 | 24.057
Number | 48 | 38 | // Circuits | 2 |  |  | Distrib. Factor | 0.95544 | AC
Kind | Open | Trapeze | Connection | Wye |  |  | Wind. Factor | 0.79436 | 596.099
Skew | - | 0 | MCL | 1225 | 680 |  | Reactance | (Coeff.: 0.0418)
Depth | 62.5 | 36.41 | No.Cond./Ph. | 192 |  |  |  | Running | Start | [5 empty] | 71.2
Width | 10.20 - 10.20 |  | Res. (20°C) | 0.11174 |  |  | Stator Slot | 18.5331 | 18.5331
Opening | 14.5 | 3 | (105°C) | 0.14905 | 0.097229 | 0.012154 | Rotor Slot | 16.8041 | 14.8054
Tip Depth | 2.83 | 3 | Material | CU | CU | CU | Zigzag | 4.1275 | 3.8445
T.Min.Wid. | 10.0437 | 10.3166 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 24.3666 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 7.1922 | 6.6991
Up. R. | - | 4.72 | Weight (kg) |  |  |  | Total Resist. | 0.25844 | 0.66358
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 230.0125 | 77.023 | 26.4494 | Total React. | 2.9696 | 2.8536
Duct | 7 x 10 | 7 x 10 | Wire 2 | - | - | - | Impedance | 2.9809 | 2.9297
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 33.372 |  | Length | Section | Density | AT | Volume | Loss |  | 3575.4 | 125RPM |  | Kline/in2
| Reac.= | 33.3991 | Primary Core | 52.6216 | 695.64 | 16.3419 | 686.4817 | 63923.4102 | 5025.4402 |  | 3580.3 | 100RPM |  | 105.4314
Excitation Data |  |  | Tooth | 6.25 | 986.3689 | 11.5252 | 22.8196 | 12329.6116 | 550.5322 |  | 3585.0 | 75RPM |  | 74.3559
Excit.Amps | 29.566 / 24.684 |  | Second.Core | 23.2148 | 704.8334 | 16.1287 | 286.4597 | Total | 5575.9724 |  | 3589.7 | 50RPM |  | 104.0562
Core Loss | 1.563 / 1.305 | Flux / Pole | Tooth | 3.641 | 802.0958 | 14.173 | 26.0241 | C.L.C. | 1.75 / 0.85 |  | 3594.3 | 25RPM |  | 91.4383
NoLoad | 29.61 / 24.72 | 11.3681 | Air Gap | 0.33 | 2168.2876 | 5.2429 | 1376.8122 | S.F.C. | 6.05 |  |  |  |  | 33.825
Load Characteristics |  |  | Temp. Rise @ 100%: | 67 / 61 |  | No Load Loss | 24635.6 / 21650.4 | W.Loss | 9758.0 / 4713.1
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 6646.9 / 6449.1 | S.Loss | 1084.7 / 523.9
Current (A) | 44.41 / 44.82 | 67.36 / 67.98 | 93.83 / 94.70 | 121.92 / 123.06 | 151.14 / 152.55 | Second. Loss | 4085.3 / 4243.7 | Total C.Loss | 10842.6 / 5237.0
Efficiency | 0.880 / 0.878 | 0.932 / 0.929 | 0.948 / 0.946 | 0.955 / 0.953 | 0.958 / 0.956 | Frict.& Wind. | 13500.0 / 17822.6 | Stray Loss | 3059.4827 | 0.955 | 0.953 | 0.99791 | Eff.
P.F. | 0.689 / 0.684 | 0.858 / 0.852 | 0.907 / 0.901 | 0.924 / 0.918 | 0.929 / 0.923 | Starting Data |  | Slip | PF | 0.924 | 0.918 | 0.99351 | PF.
Slip | 0.0014 / 0.0016 | 0.0027 / 0.0029 | 0.0040 / 0.0042 | 0.0053 / 0.0055 | 0.0066 / 0.0068 | LRA | 788.3 / 761.8 |  |  | 121.92 | 123 | 1.0089 | Current
RPM | 3595.0 / 3594.3 | 3590.4 / 3589.7 | 3585.7 / 3585.0 | 3581.0 / 3580.3 | 3576.1 / 3575.4 | % | 646.6 / 624.8 |  |  | 3581.0 | 3580 | 0.99972 | RPM
L (Inv., MH) | 6.8955 | 6.8955 | 6.8955 | 6.8955 | 6.8955 | LRT (kg.m) | 260.0 / 183.9 |  | 0.22651
(No Load) | 6.8955 |  | Correlated to: lab 1125 1126.dat |  |  | % | 128.2 / 90.6
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 2465.7767 | 0.036787 | 0.63961
IM/IW | 0.26498 | I*R1/E | 0.0077961 | Rosenberg | 316.6379 | % | 328.8 / 219.7
IW*X/E | 0.14347 | I*R2/E | 0.0052846 | Schwisky | 587.6317 | Amps | 535.953 |  |  | HP0.95 | 707.9458
SUM | 0.40845 | Friction/OP. | 0.018097 | Tsurumi | 249.3107 | Max. Output | 2376.8153 | 0.035396 | 0.65277 | HP1.5 | 31622.7766
IH/I | 0.012943 | Total | 0.04412 | Thrust (1mm) | 66.0551 | % | 318.608 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.95588 | Thrust (3 mm) | 166.1524 | Amps | 525.5349 |  |  | (RPM/1000)1.8 | 10.031
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 38 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.071705 | Coil Cur. Density |  | k | 0.0685
Depth | 36.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 59716.1664 | 3.32 / 3.36 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 32.4184 | Bar Cur. Den. |  | Load Inertia | 667.617
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 197516 | UB: 4.42 / 4.46 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.68741 | UER: 4.65 / 4.69 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.24071 | 0.7 | 90.038 | 611.8399
0.008 | 114.6071 | 161.611 | 0.8 | 90.0507 | 614.7445
0.04 | 215 | 479.3803 | 0.9 | 90.0688 | 617.2852
0.091429 | 142.3158 | 559.4377 | 1 | 90 | 619.5122
0.14286 | 112.0033 | 580.264
0.19429 | 100.0038 | 588.5935 | Acceleration Data (FV / 0.80 V)
0.29714 | 92.8309 | 596.0881 | Load Type: | Fan / Pump
0.4 | 90 | 600.7646 | Load Inertia: | 37.4 kg.m²
0.5 | 90.0208 | 604.8375 | Accel. Time: | 4.8 / 11.4 (s)
0.6 | 90.0285 | 608.537 | Rated Torque: | 202.9 kg.m
Load | Torque 80% | LRA 80%
100 | 0 | 23.6859
98.4 | 73.3485 | 129.2888
89.75 | 137.6 | 383.5043
76.2286 | 91.0821 | 447.5502
62.8571 | 71.6821 | 464.2112
51.2571 | 64.0024 | 470.8748
33.4857 | 59.4118 | 476.8705
22 | 57.6 | 480.6117
14 | 57.6133 | 483.87
8 | 57.6182 | 486.8297
6 | 57.6243 | 489.4719
8 | 57.6324 | 491.7956
15 | 57.6441 | 493.8282
30 | 57.6 | 495.6098

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | BS2M20U | [5 empty] | HRW / Model Number: | M203TCQL11F-C
Type: TIKE - Form: FCKNW - 2 Pole - 1000 HP - 4000 V - 60 Hz - 5811/12UDZ - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | NCB1 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 3.3 |  | No load amps |  |  |  | 25 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 510 |  | No load watts |  |  |  | 21650 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 12 |  | Impedance amps |  | 3 | f | 227 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.072"x.204")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 29592 | - |  | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [6 empty] | Dry Kiln
Connection |  | 2 x Wye |  |  | Winding |  | 80/115 | 67 / 88 | -
MCL |  | 1225 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 10.9788 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 24 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 123 |  | 799.5
Coil grouping |  | - |  |  |  | RPM |  | 3580
Coil pitch (slot number) |  | 1 ~ 16 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.1117 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 506 |  |  |  | Nom.Eff. (%): |  | 95 |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | 91.5
FL / LR |  | 336 / 2082 | 446 / 469
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 762 | - | 619.5122
[6 empty] | LRT (%) | 60 | 90 | -
[6 empty] | BDT (%) | 175 | 219 | -
[6 empty] | SLIP (%) |  | 0.55 | -
[5 empty] | IEEE-B | Eff. (%) |  | 95.3 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 91.8 | -
|  |  |  | Losses (Watts) |  | Primary |  | 6449 | -
[6 empty] | Secondary |  | 4244 | -
[6 empty] | Core |  | 5237 | -
[6 empty] | F & W |  | 17823 | -
[6 empty] | Stray |  | 3059 | -
End Ring (Reference) |  |  |  | Note
|  |  |  | LINK: | BS2800U.rat & LAB 8292.dat |  |  |  | H040052.rat with lab 1125 1126.dat
Run BS2M20U.rat --> update wire size
RSO2: 400-N158-03 REF ONLY
TOP HAT: 135-N201-121USS GREATER THAN 85dBA BUT LESS THAN 90dBA
TOP- HAT 135-N213-112316 FOR 85dBA
Approved |  | Design | Z. XIE
Date |  | Date | 2019-01-18 |  | REV0. FIRST ISSUE
REV1. RECORRELATE WITH H040052.rat with lab 1125 1126.dat
JROD 08/08/2024
281.0
25.0
50.0
70.0
36.41
3.00
3.00
14.12
4.72
62.5
2.83
14.5
311-
411-
051-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | ILLINOIS ELECTRIC WORKS
| TIC SR No.: | 2338072.1
MOTOR NAMEPLATE DATA
| H.P.: | 1000 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812USS |  | ENCL: | TEFC |  | FLAMPS: | 123 |  |  | FLRPM: | 3580
| FORM: | FCKNW |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40 |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10138469 |  |  |  |  | kW: | -
| NOM. EFF.: | 95 |  | MIN. EFF.: | - |  | P.F.: | 91.5
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 762 |  |  | FULL LOAD (lb-ft.): | 1467 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 90 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 215
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.3 | [5 empty] | FULL LOAD: | 91.8
|  | 3/4 LOAD: | 94.6 | [5 empty] | 3/4 LOAD: | 90.2
|  | 1/2 LOAD: | 93 | [5 empty] | 1/2 LOAD: | 85.2
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Jerry R
[9 empty] | DATE: | 2024-08-08
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | A1-10138469 |  |  | FLAmps: | 123 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1000 | Rotor Inertia: | 192.3 lb-ft² | Date: | 2024-08-08
FLRPM: | 3580 | Load Inertia: | 222.0 lb-ft² | File: | BS2M20U
| Locked Rotor Amps: | 762 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 90% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 215% | Accel. Time: | 5 / 12 (s)
| Rated Torque: | 1467 lb-ft
Comments: | PROJECT | 2338072.1 |  | D.E.Curve #: | BS2M20U
|  | Prepared by: | Jerry R | Checked by:
|  |  | Load | Torque 80% | LRA 80%
100 | 0 | 0.24071 | 100 | 0 | 23.6859
99.2 | 114.6071 | 161.611 | 98.4 | 73.3485 | 129.2888
96 | 215 | 479.3803 | 89.75 | 137.6 | 383.5043
90.8571 | 142.3158 | 559.4377 | 76.2286 | 91.0821 | 447.5502
85.7143 | 112.0033 | 580.264 | 62.8571 | 71.6821 | 464.2112
80.5714 | 100.0038 | 588.5935 | 51.2571 | 64.0024 | 470.8748
70.2857 | 92.8309 | 596.0881 | 33.4857 | 59.4118 | 476.8705
60 | 90 | 600.7646 | 22 | 57.6 | 480.6117
50 | 90.0208 | 604.8375 | 14 | 57.6133 | 483.87
40 | 90.0285 | 608.537 | 8 | 57.6182 | 486.8297
30 | 90.038 | 611.8399 | 6 | 57.6243 | 489.4719
20 | 90.0507 | 614.7445 | 8 | 57.6324 | 491.7956
10 | 90.0688 | 617.2852 | 15 | 57.6441 | 493.8282
0 | 90 | 619.5122 | 30 | 57.6 | 495.6098

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | A1-10138469 |  |  | FLAmps: | 123 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1000 | Rotor Inertia: | 192.3 lb-ft² | Date: | 2024-08-08
FLRPM: | 3580 | Load Inertia: | 222.0 lb-ft² | File: | BS2M20U
Comments: | PROJECT | 2338072.1 |  | D.E.Curve #: | BS2M20U
|  | Prepared by: | Jerry R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
619.5122 | 30 | 15 |  | 619.5122 | 0.0001 | 495.6098 | 0.0001
600 | 31.9829 | 15.9915 |  | 618.374 | 0.50548 | 494.6992 | 1.2179
500 | 46.0554 | 23.0277 |  | 616.0163 | 0.93875 | 492.813 | 2.2618
400 | 71.9616 | 35.9808 |  | 613.252 | 1.3493 | 490.6016 | 3.2511
300 | 127.9318 |  |  | 610.1626 | 1.7599 | 488.1301 | 4.2403
200 | 287.8465 |  |  | 606.6667 | 2.1911 | 485.3333 | 5.2793
215 | 249.083 | 124.5415 |  | 602.7642 | 2.6646 | 482.2114 | 6.4201
180 | 378.8551 | 177.683 |  | 598.4553 | 3.2155 | 478.7642 | 7.7474
145 | 547.6271 | 273.8136 |  | 592.3577 | 3.8644 | 473.8862 | 9.3108
125 |  | 600 |  | 584.3902 | 4.2234 | 467.5122 | 10.1758
125 |  | 1200 |  | 569.8374 | 4.5277 | 455.8699 | 10.909
125 |  | 10000 |  | 519.4309 | 4.7113 | 415.5447 | 11.3514
|  |  |  | 320.4878 | 4.866 | 256.3902 | 11.7242
|  |  |  | 120 | 4.9806 | 120 | 12.0001

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | A1-10138469 |  |  | FLAmps: | 123 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1000 | Rotor Inertia: | 192.3 lb-ft² | Date: | 2024-08-08
FLRPM: | 3580 | Load Inertia: | 222.0 lb-ft² | File: | BS2M20U
| Locked Rotor Amps: | 762 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 90% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 215% | Accel. Time: | 5 / 12 (s)
| Rated Torque: | 1467 lb-ft
Comments: | PROJECT | 2338072.1 |  | D.E.Curve #: | BS2M20U
|  | Prepared by: | Jerry R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 29.8709 | 100 | 1.0825
25 | 87.7938 | 68.4517 | 44.8019 | 79.8278 | 10.6233
50 | 92.9744 | 85.2286 | 67.9557 | 64.4048 | 20.0627
75 | 94.6411 | 90.1578 | 94.6634 | 48.7201 | 29.564
100 | 95.3384 | 91.8357 | 123.0056 | 33.0037 | 39.1304
125 | 95.6316 | 92.3173 | 152.486 | 16.833 | 48.763
3600
3597
3594
3591
3588
3585
3582
3579
3576
3573
3570
RPM
2000
1000
800
600
400
200
Input Watts (kW)
1200
1400
1600
1800
EFF.
P.F.
RPM
AMPS
WATTS
0

## StallTime
Rating: | 2 Pole - 1000.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 222.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~360 | 90.0 | 22.5 | 0.490 | 760.6 | 127.1 | 409.9
360~720 | 90.1 | 11.5 | 0.420 | 757.7 | 108.4 | 317.1
720~1080 | 90.0 | 7.0 | 0.398 | 754.3 | 101.8 | 266.9
1080~1440 | 90.0 | 7.0 | 0.398 | 750.5 | 100.8 | 233.5
1440~1800 | 90.0 | 11.0 | 0.418 | 746.2 | 104.8 | 210.2
1800~2160 | 90.0 | 18.0 | 0.459 | 741.4 | 113.6 | 192.2
2160~2530 | 91.4 | 27.7 | 0.534 | 736.1 | 130.3 | 173.8
2530~2901 | 96.4 | 42.4 | 0.629 | 728.6 | 151.3 | 157.1
2901~3086 | 106.0 | 57.1 | 0.348 | 718.8 | 81.4 | 122.2
3086~3271 | 127.2 | 69.5 | 0.295 | 700.9 | 67.2 | 85.4
3271~3456 | 178.7 | 83.0 | 0.178 | 638.9 | 37.6 | 41.8
3456~3571 | 164.8 | 94.1 | 0.150 | 394.2 | 23.3 | 37.4
3571~3581 | 107.3 | 99.2 | 0.111 | 117.6 | 0.7 | 23.0
Acceleration Time: 4.8 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 1148 kW / s |  | 13°C |  | 26°C
Rotor Bar Rise | 2018 kW / s |  | 68°C |  | 136°C
End Ring Rise | 252 kW / s |  | 25°C |  | 50°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 3.4°C / s |  | 301.7 kW | 160°C | 47.0 s
Rotor Bar | 20.1°C / s |  | 596.8 kW | 260°C | 12.9 s
Rotor ER | 7.3°C / s |  | 74.6 kW | 180°C | 24.6 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 67°C + |  | 93°C + | 40°C | = 200°C | 27.3 s
Rotor Bar | 89°C + |  | 171°C + | 40°C | = 300°C | 8.5 s
Rotor ER | 89°C + |  | 91°C + | 40°C | = 220°C | 12.4 s
Cold Stall Time: | 20.6 s |  | Hot Stall Time: |  | 10.4 s

## Circuit Param
TOSHIBA INTERNATIONAL CORPORATION | [6 empty] | INDEX | MPCF-1109
Industrial Division / Houston Motor Plant | [6 empty] | SHEET NO. | 1 of 1
[7 empty] | ISSUED | 2004-11-18
EQUIVALENT CIRCUIT DATA | [6 empty] | SUPERSEDES | NEW
[7 empty] | REVISION | REV. 0
[7 empty] | WRITTEN BY | MDC
All Values are Presented in Ohms/Phase, Equivalent Wye Connection. | [6 empty] | APPROVED BY | Paul Anderson
| CUSTOMER: | ILLINOIS ELECTRIC WORKS
| TIC SR No.: | 2338072.1
MOTOR NAMEPLATE DATA
| H.P.: | 1000 | VOLTS: | 4000 | 3 PH / | 60 Hz |  | S. RPM: | 3600
| FRAME: | 5812USS | ENCL: | TEFC | FLAMPS: | 123 |  | FLRPM: | 3580
| FORM: | FCKNW | S.F.: | 1.0 | NEMA DESIGN: | - |  | INSUL CLASS: | F
| TYPE: | TIKE | AMB.: | 40 | CODE: | F |  | DUTY: | Cont.
| MODEL No.: | A1-10138469 |  |  | kW: | -
| NOM. EFF.: | 95 | MIN. EFF.: | - | P.F.: | 91.5
Primary Resistance (R1) : |  |  |  | 0.14905
Secondary Resistance (R2) : |  |  |  | 0.10938
Starting Resistance (R3) : |  |  |  | 0.51453
Primary Reactance (X1) : |  |  |  | 2.53
Secondary Reactance (X2) : |  |  |  | 1.91
Starting Reactance (X3) : |  |  |  | 1.152
Magnetizing Reactance (Xm) : |  |  |  | 74.5
Transient Reactance : |  |  |  | 4.39
Sub Transient Reactance : |  |  |  | 3.24
Short Circuit Time Constant : |  |  |  | 0.106
Sub Transient Time Constant : |  |  |  | 0.011
Open Circuit Time Constant : |  |  |  | 1.853
[6 empty] | CERTIFIED BY: | JERRY R
[6 empty] | DATE: | 2024-08-08

## Performance API
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1082
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 2/14/02
[9 empty] | SUPERSEDES |  | NEW
[9 empty] | REVISION |  | 0
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | M. CAMPBELL
API 541 PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | P.A.A
| CUSTOMER: | ILLINOIS ELECTRIC WORKS
| TIC SR No.: | 2338072.1
MOTOR NAMEPLATE DATA
| H.P.: | 1000 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812USS |  | ENCL: | TEFC |  | FLAMPS: | 123 |  |  | FLRPM: | 3580
| FORM: | FCKNW |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40 |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10138469 |  |  |  |  | kW: | -
| NOM. EFF.: | 95 |  | MIN. EFF.: | - |  | P.F.: | 91.5
LOCKED ROTOR DATA
|  |  | AMPS AT RATED VOLTAGE: | 762 A |  |  |  | POWER FACTOR: | 14.2%
|  |  | AMPS AT 80% VOLTAGE: | 605 A
TORQUE VALUES | [6 empty] | CURVE NUMBERS
|  |  |  | FULL LOAD (LB.FT): | 1467 |  |  |  | SPEED-TORQUE CURVE: | BS2M20U
|  |  |  | LOCKED ROTOR TORQUE (% OF FLT): | 90 |  |  |  | SPEED-CURRENT CURVE: | BS2M20U
|  |  |  | PULL UP TORQUE (% OF FLT): | 90 |  |  |  | ACCELERATION CURVE: | BS2M20U
|  |  |  | BREAKDOWN TORQUE (% OF FLT): | 215
LOCKED ROTOR WITHSTAND TIMES
COLD CONDITION | [6 empty] | HOT CONDITION
|  | 100% VOLTAGE: | 30 (s) | [5 empty] | 100% VOLTAGE: | 15 (s)
|  | 90% VOLTAGE: | 37 (s) | [5 empty] | 90% VOLTAGE: | 19 (s)
|  | 80% VOLTAGE: | 47 (s) | [5 empty] | 80% VOLTAGE: | 23 (s)
|  | 70% VOLTAGE: | 62 (s) | [5 empty] | 70% VOLTAGE: | 31 (s)
DESIGN DATA
|  | MOTOR ROTOR wk2 (LB.FT2): | 192.3 | [5 empty] | NO LOAD CURRENT: | 25 A
|  | AIR GAP: | 3.3 mm | [5 empty] | ACCELERATION TIME: | 5 / 12 (s)
LOAD CHARACTERISTICS
|  |  | LOAD |  |  | 1/2 | 3/4 | FULL | SF
|  |  | AMPS (A) |  |  | 67.9 | 94.7 | 123 | -
|  |  | EFFICIENCY (%) |  |  | 92.9 | 94.6 | 95.3 | -
|  |  | POWER FACTOR (%) |  |  | 85.2 | 90.1 | 91.8 | -
|  |  | GUARENTEED EFFICIENCY (%) |  |  | - | - | - | -
EFFICIENCY TO BE DETERMINED BY IEEE 112, METHOD B
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2024-08-08
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE, FREQUENCY AND SINEWAVE POWER INPUT.