## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RAT FILES\BS2M25U.rat |  |  |  |  | Date: | 2025-04-30 | Time: | 5:49
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 1250 | 3600 | FCKNW | 4000 | 60 | 105 | 3580.1 / 3579.5 | 0.0055 / 0.0057 | 5811/12UDZ
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.5437 | LR Test Data
Air Gap | 3.3 | [5 empty] | Rt. Slot Pitch | 30.4569 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 16 | Cross Section Area |  | Mean Value | 27.5003 | 205.8387
Core Length | 600 | 600 |  |  | UB: 304.0 | UER: 1750.0 | Eff.T.W.St. | 14.3389 | WS
OD | 670 | 368.4 | Coil Pitch | 0.62494 |  |  | Eff.T.W.Rt. | 30.0388 | 36847.1931
ID | 375 | 185 | Slot Fill | - | EBL: 50.0 | ERD1: 281.0 | St.Carter Fac. | 1.1789 | IS
Core Depth | 85 | 55.29 | Con./Slot | 18 |  | ERT: 70.00 | Rt.Carter Fac. | 1.0139 | 150.8944
Eff.Core L. | 465 | 474.3 | Wire Size 1 | (.102"x.204")x1 |  | ERH: 25.00 | Carter Factor | 1.1953 | Volts / Turn
Slot Data |  |  | Wire Size 2 | (.102"x.229")x1 |  |  | Short. Factor | 0.83141 | 27.7778
Number | 48 | 38 | // Circuits | 1 |  |  | Distrib. Factor | 0.95544 | AC
Kind | Open | Trapeze | Connection | Delta |  |  | Wind. Factor | 0.79436 | 638.9372
Skew | - | 0 | MCL | 1295 | 770 |  | Reactance | (Coeff.: 0.1069)
Depth | 62.5 | 36.41 | No.Cond./Ph. | 288 |  |  |  | Running | Start
Width | 10.20 - 10.20 |  | Res. (20°C) | 0.23307 |  |  | Stator Slot | 18.5331 | 18.5331
Opening | 14.5 | 3 | (105°C) | 0.31091 | 0.24772 | 0.027346 | Rotor Slot | 16.8041 | 14.8054
Tip Depth | 2.83 | 3 | Material | CU | CU | CU | Zigzag | 4.1275 | 3.7811
T.Min.Wid. | 10.0437 | 10.3166 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 20.8428 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 7.1922 | 6.5805
Up. R. | - | 4.72 | Weight (kg) |  |  |  | Total Resist. | 0.58597 | 1.6182
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 130.4575 | 86.2657 | 26.4494 | Total React. | 7.2161 | 6.9009
Duct | 10 x 10 | 9 x 10 | Wire 2 | 146.8216 | - | - | Impedance | 7.2398 | 7.0881
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 33.372 |  | Length | Section | Density | AT | Volume | Loss |  | 3574.4 | 125RPM |  | Kline/in2
| Reac.= | 33.3991 | Primary Core | 52.6216 | 790.5 | 16.6051 | 734.3643 | 72640.2367 | 5860.4792 |  | 3579.5 | 100RPM |  | 107.1296
Excitation Data |  |  | Tooth | 6.25 | 1120.8738 | 11.7108 | 23.8954 | 14010.9219 | 642.01 |  | 3584.4 | 75RPM |  | 75.5535
Excit.Amps | 20.140 / 16.814 |  | Second.Core | 23.2148 | 816.966 | 16.0672 | 281.8446 | Total | 6502.4892 |  | 3589.3 | 50RPM |  | 103.6591
Core Loss | 1.051 / 0.878 | Flux / Pole | Tooth | 3.641 | 929.702 | 14.1189 | 25.6213 | C.L.C. | 1.75 / 0.85 |  | 3594.2 | 25RPM |  | 91.0893
NoLoad | 34.93 / 29.16 | 13.1263 | Air Gap | 0.33 | 2488.6028 | 5.2746 | 1385.1368 | S.F.C. | 6.05 |  |  |  |  | 34.0295
Load Characteristics |  |  | Temp. Rise @ 100%: | 72 / 67 |  | No Load Loss | 26412.7 / 23212.2 | W.Loss | 11379.4 / 5496.2
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 7079.5 / 6868.8 | S.Loss | 1249.8 / 603.6
Current (A) | 53.41 / 53.89 | 82.49 / 83.23 | 115.74 / 116.77 | 150.89 / 152.24 | 187.41 / 189.08 | Second. Loss | 5315.8 / 5521.9 | Total C.Loss | 12629.1 / 6099.9
Efficiency | 0.895 / 0.893 | 0.940 / 0.938 | 0.955 / 0.953 | 0.961 / 0.959 | 0.963 / 0.961 | Frict.& Wind. | 13500.0 / 17822.6 | Stray Loss | 3981.0195 | 0.961 | 0.959 | 0.99792 | Eff.
P.F. | 0.704 / 0.699 | 0.867 / 0.862 | 0.913 / 0.907 | 0.928 / 0.922 | 0.932 / 0.926 | Starting Data |  | Slip | PF | 0.928 | 0.922 | 0.99353 | PF.
Slip | 0.0014 / 0.0016 | 0.0028 / 0.0030 | 0.0041 / 0.0043 | 0.0055 / 0.0057 | 0.0069 / 0.0071 | LRA | 977.4 / 944.6 |  |  | 150.89 | 152.24 | 1.0089 | Current
RPM | 3594.9 / 3594.2 | 3590.0 / 3589.3 | 3585.1 / 3584.4 | 3580.1 / 3579.5 | 3575.1 / 3574.4 | % | 647.7 / 626.0 |  |  | 3580.1 | 3579.5 | 0.99983 | RPM
L (Inv., MH) | 16.759 | 16.759 | 16.759 | 16.759 | 16.759 | LRT (kg.m) | 338.6 / 239.5 |  | 0.22831
(No Load) | 16.759 |  | Correlated to: lab 1125 1126.dat |  |  | % | 133.5 / 94.4
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 3070.9915 | 0.038083 | 0.64202
IM/IW | 0.25093 | I*R1/E | 0.0067216 | Rosenberg | 364.18 | % | 327.5 / 218.9
IW*X/E | 0.14479 | I*R2/E | 0.0055193 | Schwisky | 675.8627 | Amps | 664.1236 |  |  | HP0.95 | 875.1138
SUM | 0.39573 | Friction/OP. | 0.014477 | Tsurumi | 289.6113 | Max. Output | 2956.3571 | 0.036603 | 0.65563 | HP1.5 | 44194.1738
IH/I | 0.012158 | Total | 0.038876 | Thrust (1mm) | 91.9226 | % | 317.0356 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.96112 | Thrust (3 mm) | 231.1325 | Amps | 650.8424 |  |  | (RPM/1000)1.8 | 10.031
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 38 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.072243 | Coil Cur. Density |  | k | 0.0685
Depth | 36.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 69216.4656 | 3.13 / 3.15 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 37.5758 | Bar Cur. Den. |  | Load Inertia | 790.4059
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 224450 | UB: 4.77 / 4.81 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.68741 | UER: 5.02 / 5.06 | LER: -
S-T Curve Data
Slip | Torque (%) | Amps | Slip | Torque (%) | Amps
0 | 0 | 0 | 0.7 | 149.6399 | 999.1476
0.01 | 172.3903 | 255.1276 | 0.8 | 143.9081 | 1004.1593
0.05 | 338.0136 | 773.7296 | 0.9 | 138.6226 | 1008.3632
0.1 | 259.0248 | 909.6086 | 1 | 133.8996 | 1012.2077
0.15 | 214.7214 | 945.1735
0.2 | 193.6258 | 959.3716
0.3 | 176.6134 | 972.1224
0.4 | 168.7074 | 980.1042
0.5 | 162.1601 | 987.0897
0.6 | 155.782 | 993.4547

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | BS2M25U | [5 empty] | HRW / Model Number: | M253TCQL11F-C
Type: TIKE - Form: FCKNW - 2 Pole - 1250 HP - 4000 V - 60 Hz - 5811/12UDZ - Class F | [13 empty] | Motor Type Selection |  | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  |  |  |  | EPACT |  | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [9 empty] | EQP-III |  | M36 - 26Ga.
Air Gap |  | 3.3 |  | No load amps |  |  |  | 29 | 31.26 |  |  |  |  | Exp.Prf. |  | NCB1 - 26Ga.
Stack length |  | 600 |  | No load watts |  |  |  | 23212 | 26413 |  |  |  |  | Exp.Prf.-EQPIII |  | M43 - 26Ga.
Number of turns per coil |  | 9 |  | Impedance amps |  | 3 | f | 843 | 235 |  |  |  |  | Prem. Eff. |  | M45 - 26Ga.
Wire 1 (061-0023-04) |  | (.102"x.204")x1 |  | Impedance volts |  | 3 | f | 1150 | 1150 |  |  |  |  | Standard Eff. |  | M54 - 26Ga.
Wire 2 (061-0020-07) |  | (.102"x.229")x1 |  | Impedance watts |  | 3 | f | 36847 | 86500 |  |  |  |  | OWP |  | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [9 empty] | Dry Kiln
Connection |  | 1 x Delta |  |  | Winding |  | 80/115 | 72 / 95 | -
MCL |  | 1295 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 9.4356 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.1018 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 18 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 152 |  | 988 | 975.4
Coil grouping |  | - |  |  |  | RPM |  | 3575
Coil pitch (slot number) |  | 1 ~ 16 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 | [5 empty] | Method of Connection
Resistance per phase @ 20 °C |  | 0.2331 |  |  |  | DESIGN | [7 empty] | Skip
Coil Weight | Wire1 | 287 |  |  |  | Nom.Eff. (%): | [7 empty] | Adjacent
(lbs.) | Wire2 | 323 |  |  |  | Min.Eff. (%): | [7 empty] | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | 92
FL / LR |  | 315 / 1958 | 481 / 506
Stator Slot Shape (Reference) |  |  |  | Performance |  |  |  |  | LAB N2501MTR47
[6 empty] | LRC (A) | - | 945 | 1027 | 621.7% | 675.7%
[6 empty] | LRT (%) | 60 | 94 | -
[6 empty] | BDT (%) | 175 | 218 | -
[6 empty] | SLIP (%) |  | 0.57 | -
[5 empty] | IEEE-B | Eff. (%) |  | 95.9 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 92.2 | - |  |  | N2501MTR47 | 2025-09-24 | A1-10136700
|  |  |  | Losses (Watts) |  | Primary |  | 6869 | -
[6 empty] | Secondary |  | 5522 | - |  |  | V | I | %FLA | logV | logI
[6 empty] | Core |  | 6100 | - |  |  | 2578.14 | 633.37 | 416.7% | 3.4113 | 2.8017
[6 empty] | F & W |  | 17823 | - |  |  | 2363.78 | 570.11 | 375.1% | 3.3736 | 2.756
[6 empty] | Stray |  | 3981 | - |  |  | 1918.95 | 450.801 | 296.6% | 3.2831 | 2.654
End Ring (Reference) |  |  |  | Note | RNP OF BS2M25U | [6 empty] | 1782.11 | 410.326 | 270% | 3.2509 | 2.6131
|  |  |  | LINK: | H040052.RAT & LAB 1125 & 1126.DAT | [6 empty] | 1179.32 | 260.816 | 171.6% | 3.0716 | 2.4163
[5 empty] | RSO2: 400-N157-01 | [6 empty] | 982.72 | 212.388 | 139.7% | 2.9924 | 2.3271
[5 empty] | 350-N129-05 | [6 empty] | 879.29 | 188.902 | 124.3% | 2.9441 | 2.2762
[5 empty] | TOP HAT: 135-N201-121USS GREATER THAN 85dBA BUT LESS THAN 90dBA | [6 empty] | 688.7 | 148.047 | 97.4% | 2.838 | 2.1704
TOP- HAT 135-N213-112316 FOR 85dBA
Approved |  | Design | A.GRACIA |  | NOT SUITABLE FOR API IF DOL | [6 empty] | 4000 | 1026.553 |  | 3.6021 | 3.0114
Date |  | Date | 2003-03-26 |  | REV0. FIRST ISSUE
135-N213-105 TOP HAT PRODUCED 82.2 dBA (see A1-10136699 LAB RT-51926 (new fan cover)
281.0
25.0
50.0
70.0
36.41
3.00
3.00
14.12
4.72
62.5
2.83
14.5
311-
411-
051-
Wrong End Ring Shape in .rat
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | CLYDE UNION PUMPS CANADA LTD
| TIC SR No.: | 2306938.1
MOTOR NAMEPLATE DATA
| H.P.: | 1250 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812USS |  | ENCL: | TEAAC |  | FLAMPS: | 152 |  |  | FLRPM: | 3580
| FORM: | FCKNW4 |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10134386 |  |  |  |  | kW: | -
| NOM. EFF.: | 95.8 |  | MIN. EFF.: | - |  | P.F.: | 92
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 945 |  |  | FULL LOAD (lb-ft.): | 1834 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 90 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 215
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.8 | [5 empty] | FULL LOAD: | 92.3
|  | 3/4 LOAD: | 95.2 | [5 empty] | 3/4 LOAD: | 90.8
|  | 1/2 LOAD: | 93.6 | [5 empty] | 1/2 LOAD: | 86.1
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2023-09-29
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | A1-10134386 |  |  | FLAmps: | 152
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1250 | Rotor Inertia: | 222.9 lb-ft² | Date: | 2023-09-29
FLRPM: | 3580 | Load Inertia: | 790.4 lb-ft² | File: | h040052
| Locked Rotor Amps: | 945 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 90% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 215% | Accel. Time: | 9.2 / 20.4 (s)
| Rated Torque: | 1834 lb-ft
Comments: | PROJECT | 2306938.1 |  | D.E.Curve #: | h040052
|  | Prepared by: | Zichao Xie | Checked by:
|  |  | Load | Torque 80% | LRA 80%
100 | 0 | 0.22981 | 100 | 0 | 27.9443 | -100
99.2 | 109.6521 | 156.7025 | 98.4 | 70.1774 | 125.362 | -28.2226
96 | 215 | 475.2343 | 89.75 | 137.6 | 380.1874 | 47.85
90.9474 | 146.7691 | 558.6929 | 76.4632 | 93.9322 | 446.9543 | 17.4691
85.8947 | 116.8536 | 580.5373 | 63.3263 | 74.7863 | 464.4298 | 11.46
80.8421 | 104.5785 | 589.2579 | 51.8526 | 66.9302 | 471.4063 | 15.0776
70.7368 | 97.6728 | 597.0897 | 34.2526 | 62.5106 | 477.6717 | 28.258
60.6316 | 94.6854 | 601.9922 | 22.6947 | 60.5986 | 481.5938 | 37.9039
50.5263 | 92.8601 | 606.2827 | 14.4211 | 59.4305 | 485.0262 | 45.0094
40.4211 | 91.6632 | 610.1922 | 8.2526 | 58.6645 | 488.1538 | 50.4118
30.3158 | 90.897 | 613.6888 | 6.0632 | 58.1741 | 490.9511 | 52.1109
20.2105 | 90.4271 | 616.7671 | 7.9579 | 57.8734 | 493.4137 | 49.9155
10.1053 | 90.1506 | 619.3492 | 14.9263 | 57.6964 | 495.4793 | 42.7701
0 | 90 | 621.7105 | 30 | 57.6 | 497.3684 | 27.6

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | A1-10134386 |  |  | FLAmps: | 152
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1250 | Rotor Inertia: | 222.9 lb-ft² | Date: | 2023-09-29
FLRPM: | 3580 | Load Inertia: | 790.4 lb-ft² | File: | h040052
945 A
90%
1834 lb-ft
Comments: | PROJECT | 2306938.1 |  | D.E.Curve #: | h040052
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time | CURRENT (%) | Accel. Time
621.7105 | 24.848 | 11.4836 |  | 621.7105 | 0.0001 | 621.7105 | 0.0001
600 | 26.6788 | 12.3296 |  | 620.5263 | 0.966 | 496.4474 | 1.856
500 | 38.4175 | 17.7547 |  | 618.0263 | 1.795 | 494.4737 | 3.267
400 | 60.0273 | 27.7417 |  | 615.1974 | 2.575 | 492.1711 | 4.548
300 | 106.7152 |  |  | 611.9079 | 3.352 | 489.5395 | 5.821
200 | 240.1091 |  |  | 608.2237 | 4.159 | 486.5789 | 7.19
215 | 207.7742 | 96.0232 |  | 604.1447 | 5.028 | 483.2895 | 8.764
180 | 318.2713 | 136.9961 |  | 599.5395 | 5.993 | 479.6053 | 10.737
120 | 666.9697 | 308.2411 |  | 593.1579 | 7.117 | 474.5395 | 13.747
110 |  | 700 |  | 584.8684 | 7.732 | 467.8947 | 16.203
110 |  | 1400 |  | 569.6053 | 8.26 | 455.7237 | 18.455
110 |  | 10000 |  | 516.9737 | 8.594 | 413.5526 | 19.454
|  |  |  | 315.9868 | 8.897 | 0 | 20.357
|  |  |  | 0 | 9.188

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | A1-10134386 |  |  | FLAmps: | 152
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1250 | Rotor Inertia: | 222.9 lb-ft² | Date: | 2023-09-29
FLRPM: | 3580 | Load Inertia: | 790.4 lb-ft² | File: | h040052
| Locked Rotor Amps: | 945 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 90% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 215% | Accel. Time: | 9.2 / 20.4 (s)
| Rated Torque: | 1834 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 3600 | 4000
[8 empty] | 3597 | 3600
Comments: | PROJECT | 2306938.1 |  | D.E.Curve #: | h040052 |  |  | 3594 | 3200
[8 empty] | 3591 | 2800
[8 empty] | 3588 | 2400
[8 empty] | 3585 | 2000
|  | Prepared by: | Zichao Xie | Checked by: |  | SYNC SPEED | 3600 | 3582 | 1600
[6 empty] | NEW SPEED LOWER RANGE | 3570 | 3579 | 1200
[6 empty] | NEW kW UPPER RANGE | 4000 | 3576 | 800
[8 empty] | 3573 | 400
[8 empty] | 3570 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 29 | 100 | 0.5803
25 | 89.1 | 70.3 | 53.74 | 82.4032 | 6.5436
50 | 93.7 | 86.1 | 83.41 | 66.4974 | 12.4389
75 | 95.2 | 90.7 | 116.8 | 50.2539 | 18.3489
100 | 95.8 | 92.3 | 152.12 | 33.3333 | 24.3192
125 | 96.1 | 92.7 | 188.92 | 21.1499 | 30.3332
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 35.2099 | 100 | 0.58031
25 | 88.981 | 70.326 | 53.74 | 79.1216 | 6.5458
50 | 93.6268 | 86.1213 | 83.4124 | 63.4437 | 12.442
75 | 95.1671 | 90.7511 | 116.8138 | 47.329 | 18.3609
100 | 95.7688 | 92.3267 | 152.1319 | 30.6327 | 24.3274
125 | 96.0253 | 92.6796 | 188.9348 | 18.7967 | 30.328
3600
3597
3594
3591
3588
3585
3582
3579
3576
3573
3570
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0.0

## StallTime
Rating: | 2 Pole - 1250.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 790.4 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~364 | 90.1 | 22.5 | 0.966 | 943.2 | 268.3 | 834.2
364~728 | 90.3 | 11.4 | 0.829 | 939.4 | 228.4 | 644.4
728~1091 | 90.7 | 7.0 | 0.780 | 935.1 | 213.2 | 540.1
1091~1455 | 91.3 | 7.2 | 0.777 | 930.1 | 210.1 | 471.9
1455~1819 | 92.3 | 11.3 | 0.807 | 924.5 | 215.9 | 423.0
1819~2183 | 93.8 | 18.6 | 0.869 | 918.3 | 229.3 | 382.8
2183~2547 | 96.2 | 28.5 | 0.965 | 911.3 | 251.2 | 345.0
2547~2910 | 101.1 | 43.1 | 1.124 | 901.6 | 287.9 | 308.2
2910~3092 | 110.7 | 57.6 | 0.615 | 889.0 | 153.4 | 236.4
3092~3274 | 131.8 | 69.9 | 0.528 | 865.8 | 127.7 | 166.8
3274~3456 | 180.9 | 83.1 | 0.334 | 785.8 | 74.9 | 85.1
3456~3571 | 162.3 | 94.1 | 0.303 | 480.3 | 49.1 | 78.9
3571~3580 | 104.8 | 99.2 | 0.291 | 145.6 | 2.1 | 67.3
Acceleration Time: 9.2 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2312 kW / s |  | 22°C |  | 43°C
Rotor Bar Rise | 4128 kW / s |  | 124°C |  | 249°C
End Ring Rise | 456 kW / s |  | 45°C |  | 90°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 3.1°C / s |  | 327.9 kW | 160°C | 52.1 s
Rotor Bar | 22.8°C / s |  | 755.8 kW | 260°C | 11.4 s
Rotor ER | 8.2°C / s |  | 83.4 kW | 180°C | 22.0 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 72°C + |  | 88°C + | 40°C | = 200°C | 28.6 s
Rotor Bar | 97°C + |  | 163°C + | 40°C | = 300°C | 7.2 s
Rotor ER | 97°C + |  | 83°C + | 40°C | = 220°C | 10.2 s
Cold Stall Time: | 17.4 s |  | Hot Stall Time: |  | 8.0 s