## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | Z:\Motor R&D\Active Projects\6810 Development\Electrical Design\TEAAC\2P\Series\BS2M45U.rat |  |  |  |  | Date: | 2014-10-22 | Time: | 13:36
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 2250 | 3600 | FCW4 | 4000 | 60 | 105 | 3580.4 / 3580.7 | 0.0054 / 0.0054 | 6813USS
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 26.1799 | LR Test Data
Air Gap | 3.5 | [5 empty] | Rt. Slot Pitch | 30.2549 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 18 | Cross Section Area |  | Mean Value | 28.2174 | 195.7882
Core Length | 850 | 850 |  |  | UB: 322.1 | UER: 3768.4 | Eff.T.W.St. | 17.1276 | WS
OD | 815 | 443 | Coil Pitch | 0.62957 |  |  | Eff.T.W.Rt. | 29.8593 | 57430.841
ID | 450 | 170 | Slot Fill | - | EBL: 62.5 | ERD1: 328.0 | St.Carter Fac. | 1.5285 | IS
Core Depth | 109.5 | 98.09 | Con./Slot | 22 |  | ERT: 65.54 | Rt.Carter Fac. | 1.0132 | 262.7579
Eff.Core L. | 639.84 | 695.64 | Wire Size 1 | (.072"x.258")x2 |  | ERH: 57.50 | Carter Factor | 1.5488 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.83543 | 40.404
Number | 54 | 46 | // Circuits | 2 |  |  | Distrib. Factor | 0.95529 | AC
Kind | Open | Trapeze | Connection | Delta |  |  | Wind. Factor | 0.79808 | 637.4298
Skew | - | 0 | MCL | 1717 | 1040.537 |  | Reactance | (Coeff.: 0.0624)
Depth | 73 | 38.41 | No.Cond./Ph. | 198 |  |  |  | Running | Start
Width | 17.30 - 17.30 |  | Res. (20°C) | 0.12681 |  |  | Stator Slot | 14.9933 | 14.9933
Opening | 17.3 | 3 | (105°C) | 0.16916 | 0.12467 | 0.026712 | Rotor Slot | 16.3182 | 13.7978
Tip Depth | 13.15 | 3 | Material | CU | CU | CU | Zigzag | 4.6908 | 4.2866
T.Min.Wid. | 8.8799 | 10.8884 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 21.2927 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 6.7858 | 6.2091
Up. R. | - | 5.72 | Weight (kg) |  |  |  | Total Resist. | 0.32054 | 0.83178
Wedge Dep. | 0.80 - 2.40 | Normal | Wire 1 | 423.4408 | 145.7097 | 84.5315 | Total React. | 4.0004 | 3.7813
Duct | 27 x 6 | 17 x 6 | Wire 2 | - | - | - | Impedance | 4.0132 | 3.8717
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.3592 |  | Length | Section | Density | AT | Volume | Loss
| Reac.= | 35.3955 | Primary Core | 64.0099 | 1401.2497 | 13.5621 | 384.1468 | 155285.9088 | 9025.3837
Excitation Data |  |  | Tooth | 7.3 | 1534.0661 | 12.3879 | 32.3684 | 22397.3656 | 1124.1345
Excit.Amps | 25.349 / 25.388 |  | Second.Core | 28.7597 | 1758.9026 | 10.8044 | 86.9587 | Total | 10149.5182
Core Loss | 1.965 / 1.968 | Flux / Pole | Tooth | 3.841 | 1742.1171 | 10.9085 | 11.9465 | C.L.C. | 1.75 / 0.71
NoLoad | 44.04 / 44.10 | 19.0039 | Air Gap | 0.35 | 3276.9399 | 5.7993 | 1615.2233 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 76 / 75 |  | No Load Loss | 33255.9 / 49408.8 | W.Loss | 17761.7 / 7234.2
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 11679.9 / 11796.9 | S.Loss | 5842.2 / 2379.5
Current (A) | 81.62 / 84.25 | 137.83 / 142.28 | 199.10 / 205.53 | 262.76 / 271.25 | 328.43 / 339.04 | Second. Loss | 9370.1 / 8890.2 | Total C.Loss | 23603.9 / 9613.7
Efficiency | 0.923 / 0.909 | 0.956 / 0.941 | 0.966 / 0.951 | 0.969 / 0.954 | 0.970 / 0.955 | Frict.& Wind. | 9407.5 / 29927.4 | Stray Loss | 20410.0078
P.F. | 0.804 / 0.791 | 0.919 / 0.904 | 0.945 / 0.930 | 0.951 / 0.936 | 0.951 / 0.935 | Starting Data |  | Slip | PF
Slip | 0.0014 / 0.0013 | 0.0027 / 0.0026 | 0.0040 / 0.0040 | 0.0054 / 0.0054 | 0.0068 / 0.0067 | LRA | 1789.4 / 1737.5
RPM | 3595.1 / 3595.4 | 3590.3 / 3590.6 | 3585.4 / 3585.7 | 3580.4 / 3580.7 | 3575.5 / 3575.8 | % | 681.0 / 661.3
L (Inv., MH) | 9.004 | 9.004 | 9.004 | 9.004 | 9.004 | LRT (kg.m) | 575.2 / 469.8 |  | 0.21484
(No Load) | 9.004 |  | Correlated to: P148450_TEAAC_CStubes_Lab1317.dat |  |  | % | 126.0 / 102.9
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 5606.2075 | 0.037808 | 0.64965
IM/IW | 0.17647 | I*R1/E | 0.006409 | Rosenberg | 726.9212 | % | 332.2 / 251.5
IW*X/E | 0.14365 | I*R2/E | 0.0054361 | Schwisky | 1041.1859 | Amps | 1198.4757
SUM | 0.32013 | Friction/OP. | 0.0056047 | Tsurumi | 355.7939 | Max. Output | 5398.415 | 0.03635 | 0.66331
IH/I | 0.012966 | Total | 0.030416 | Thrust (1mm) | 262.7608 | % | 321.6214
|  | Efficiency | 0.96958 | Thrust (3 mm) | 670.3262 | Amps | 1174.6997
Single Cage Data | [5 empty] | Miscellaneous Data
Slot Number | 46 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.068137 | Coil Cur. Density
Depth | 38.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 146794.252 | 3.25 / 3.35
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 115.2329 | Bar Cur. Den.
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 456986.8 | UB: 4.60 / 4.74 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.69435 | UER: 2.88 / 2.97 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.16249 | 0.68737 | 100.8393 | 632.1025
0.002 | 128.2599 | 159.759 | 0.79158 | 100.3909 | 635.6649
0.01 | 250 | 484.3136 | 0.89579 | 100.1366 | 638.7053
0.062105 | 152.7565 | 568.6079 | 1 | 100 | 641.3284
0.11421 | 126.2219 | 591.0354
0.16632 | 114.8871 | 600.5502 | Acceleration Data (FV V)
0.27053 | 108.0797 | 610.3591 | Load Type: | Fan / Pump
0.37474 | 104.8206 | 617.1758 | Load Inertia: | 99.5 kg.m²
0.47895 | 102.8399 | 622.9518 | Accel. Time: | 5.7 (s)
0.58316 | 101.5985 | 627.901 | Rated Torque: | 456.6 kg.m
Load
100
99.6
98
83.8526
70.3053
57.4105
38.0105
24.7789
15.6842
9.0105
6.2526
7.8316
14.7053
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | BS2M45U | [5 empty] | HRW / Model Number: | M453TCQL11F-C
Type: TIKE - Form: FCW4 - 2 Pole - 2250 HP - 4000 V - 60 Hz - 6813USS - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M36 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 3.5 |  | No load amps |  |  |  | 44 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 850 |  | No load watts |  |  |  | 39795 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 11 |  | Impedance amps |  | 3 | f | 431 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.072"x.258")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 130566 | - |  | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 2 x Delta |  |  | Winding |  | 80/115 | 75 / 100 | -
MCL |  | 1717 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 15.2164 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7936 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 22 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 271 |  | 1761.5
Coil grouping |  | - |  |  |  | RPM |  | 3581
Coil pitch (slot number) |  | 1 ~ 18 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.13125 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 958 |  |  |  | Nom.Eff. (%): |  |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 335 / 2148 | 474 / 297
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 1738 | - | 641.3284
[6 empty] | LRT (%) | 60 | 102 | -
[6 empty] | BDT (%) | 175 | 251 | -
[6 empty] | SLIP (%) |  | 0.54 | -
[5 empty] | IEEE-B | Eff. (%) |  | 95.4 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 93.6 | -
|  |  |  | Losses (Watts) |  | Primary |  | 11797 | -
[6 empty] | Secondary |  | 8890 | -
[6 empty] | Core |  | 9614 | -
[6 empty] | F & W |  | 29927 | -
[6 empty] | Stray |  | 20410 | -
End Ring (Reference) |  |  |  | Note
Outer Fan: DT360
Limits: BS2M45U
Approved |  | Design | Mario L
Date |  | Date | 2014-10-22 |  | Rev 0: First Issue
38.41
3.00
3.00
14.12
5.72
73.0
13.15
17.3
051-TA13
411-TA13
311-TA13
328.0
62.5
85.0
57.5
55
.0
18.50
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## Form
Winding Data Calculation
MCL: 1717.0
Coil Resistance |  |  | Lead Resistance
11T: | 0.0290 ~ 0.0279 |  | AWG. (1/0 x 2) x 3
0.0007
Coil Dimensions
HM: | 11T: 22.32 | WM: | 11T: 13.51 | WT:
17.40 ~ 17.00
Insulation Allowance |  |  | Wire Weight
Depth: | 15.22 |  | (.072"x.258")x 2: |  | 958 lbs.
Width: | 3.79
QC Resistance
1-2, 2-3, 3-1: |  | 0.090 ~ 0.085

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | M453TCQL11F-C |  |  | FLAmps: | 271
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 6813USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2250 | Rotor Inertia: | 683.6 lb-ft² | Date: | 2014-10-22
FLRPM: | 3581 | Load Inertia: | N/A | File: | BS2M45U
| Locked Rotor Amps: | 1738 A | Load Type: | N/A
| Locked Rotor Torque: | 100% | Starting at: | N/A
| Breakdown Torque: | 250% | Accel. Time: | N/A
| Rated Torque: | 3300 lb-ft
Comments: |  |  |  | D.E.Curve #: | BS2M45U
|  | Prepared by: | Mario L | Checked by:
100 | 0 | 0.16249
99.8 | 128.2599 | 159.759
99 | 250 | 484.3136
93.7895 | 152.7565 | 568.6079
88.5789 | 126.2219 | 591.0354
83.3684 | 114.8871 | 600.5502
72.9474 | 108.0797 | 610.3591
62.5263 | 104.8206 | 617.1758
52.1053 | 102.8399 | 622.9518
41.6842 | 101.5985 | 627.901
31.2632 | 100.8393 | 632.1025
20.8421 | 100.3909 | 635.6649
10.4211 | 100.1366 | 638.7053
0 | 100 | 641.3284

## StallTime
Rating: | 2 Pole - 2250.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 590.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~375 | 100.1 | 22.4 | 0.605 | 1734.4 | 309.3 | 1276.7
375~750 | 100.3 | 11.3 | 0.529 | 1726.8 | 267.9 | 999.8
750~1125 | 100.6 | 7.0 | 0.503 | 1717.8 | 252.3 | 842.2
1125~1501 | 101.2 | 7.6 | 0.503 | 1707.3 | 249.4 | 734.6
1501~1876 | 102.2 | 12.3 | 0.523 | 1694.9 | 256.3 | 653.8
1876~2251 | 103.8 | 20.2 | 0.563 | 1680.4 | 271.3 | 584.4
2251~2626 | 106.5 | 31.4 | 0.626 | 1663.3 | 296.4 | 518.8
2626~3001 | 111.5 | 47.7 | 0.737 | 1640.8 | 341.2 | 454.6
3001~3189 | 120.6 | 63.9 | 0.415 | 1614.6 | 185.9 | 334.3
3189~3376 | 139.5 | 77.1 | 0.377 | 1571.3 | 163.6 | 229.2
3376~3564 | 201.4 | 90.9 | 0.213 | 1426.7 | 85.5 | 85.2
3564~3593 | 189.1 | 98.8 | 0.040 | 872.7 | 11.7 | 27.5
3593~3600 | 114.1 | 99.8 | 0.063 | 276.1 | 0.8 | 48.4
Acceleration Time: 5.7 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2692 kW / s |  | 17°C |  | 33°C
Rotor Bar Rise | 5591 kW / s |  | 100°C |  | 199°C
End Ring Rise | 1198 kW / s |  | 37°C |  | 74°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 3.7°C / s |  | 609.4 kW | 160°C | 42.8 s
Rotor Bar | 24.6°C / s |  | 1382.3 kW | 260°C | 10.6 s
Rotor ER | 9.1°C / s |  | 296.2 kW | 180°C | 19.8 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 75°C + |  | 85°C + | 40°C | = 200°C | 22.7 s
Rotor Bar | 101°C + |  | 159°C + | 40°C | = 300°C | 6.4 s
Rotor ER | 101°C + |  | 79°C + | 40°C | = 220°C | 8.6 s
Cold Stall Time: | 20.5 s |  | Hot Stall Time: |  | 9.0 s

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | M453TCQL11F-C |  |  | FLAmps: | 271
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 6813USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2250 | Rotor Inertia: | 683.6 lb-ft² | Date: | 2014-10-22
FLRPM: | 3581 | Load Inertia: | 590.0 lb-ft² | File: | BS2M45U
Comments: |  |  |  | D.E.Curve #: | BS2M45U
|  | Prepared by: | Mario L | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
641.3284 | 29.3526 | 12.8065 |  | 641.3284 | 0.0001
600 | 33.5355 | 14.6316 |  | 640 | 0.605
500 | 48.2912 | 21.0694 |  | 637.1956 | 1.134
400 | 75.4549 | 32.921 |  | 633.8745 | 1.637
300 | 134.1421 |  |  | 630 | 2.14
200 | 301.8197 |  |  | 625.4244 | 2.663
250 | 193.1646 | 84.2777 |  | 620.0738 | 3.226
180 | 425.717 | 162.5728 |  | 613.7638 | 3.852
145 | 574.2111 | 250.5284 |  | 605.4613 | 4.589
125 |  | 600 |  | 595.7934 | 5.004
125 |  | 1200 |  | 579.8155 | 5.381
125 |  | 10000 |  | 526.4576 | 5.594
|  |  |  | 322.0295 | 5.634
|  |  |  | 0 | 5.697

## MagNoise
Magnetic Noise Verification
Rating: | 2 Pole - 2250.0 HP - 3600 RPM - 4000 V - 60 Hz
Electromagnetic Excitation Frequencies
| L = | 0 | L = | + 1 | L = | - 1 | Slip = | 0 | Slip = | 0.005
Mode A | 6 |  | 12 |  | 0 |  | 2880.0 Hz |  | 2865.0 Hz
Mode B | 10 |  | 16 |  | 4 |  | 2640.0 Hz |  | 2625.0 Hz
Mode C | 8 |  | 14 |  | 2 |  | 2760.0 Hz |  | 2745.0 Hz
Natural Frequencies of Stator Core
| Mode 0 = |  | 1483.0 Hz |  | Mode 6 = |  | 4554.3 Hz
| Mode 2 = |  | 354.0 Hz |  | Mode 7 = |  | 6268.4 Hz
| Mode 3 = |  | 1001.2 Hz |  | Mode 8 = |  | 8246.6 Hz
| Mode 4 = |  | 1919.7 Hz |  | Mode 9 = |  | 10488.8 Hz
| Mode 5 = |  | 3104.5 Hz |  | Mode 10 = |  | 12995.0 Hz
Analysis Results
No matching frequencies detected.

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | M453TCQL11F-C |  |  | FLAmps: | 271
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 6813USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2250 | Rotor Inertia: | 683.6 lb-ft² | Date: | 2014-10-22
FLRPM: | 3581 | Load Inertia: | N/A | File: | BS2M45U
| Locked Rotor Amps: | 1738 A | Load Type: | N/A
| Locked Rotor Torque: | 100% | Starting at: | N/A
| Breakdown Torque: | 250% | Accel. Time: | N/A
| Rated Torque: | 3300 lb-ft
Comments: |  |  |  | D.E.Curve #: | BS2M45U
|  | Prepared by: | Mario L | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 45.4584 | 100 | 0.6632
25 | 90.9147 | 79.0927 | 84.2526 | 84.6552 | 7.6944
50 | 94.1277 | 90.472 | 142.2826 | 68.6715 | 14.8636
75 | 95.0706 | 93.0139 | 205.5326 | 52.4277 | 22.0742
100 | 95.4032 | 93.645 | 271.2477 | 35.7666 | 29.3297
125 | 95.4819 | 93.5738 | 339.0381 | 19.4117 | 36.6319
3600
3597
3594
3591
3588
3585
3582
3579
3576
3573
3570
RPM
6000
3000
2400
1800
1200
600
Input Watts (kW)
3600
4200
4800
5400
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 11/08/96
[9 empty] | SUPERSEDES |  | 10/06/95
[9 empty] | REVISION |  | 1
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | R. EVANS
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | Jay Bugbee
CUSTOMER:
TIC SR No.:
MOTOR NAMEPLATE DATA
| H.P.: | 2250 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 6813USS |  | ENCL: | TEAAC |  | FLAMPS: | 271 |  |  | FLRPM: | 3581
| FORM: | FCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | M453TCQL11F-C |  |  |  |  | kW:
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 1738 |  |  | FULL LOAD (lb-ft.): | 3300 |  |  | DRIVE END: | M9-90 INS
[6 empty] | LOCKED ROTOR (%): | 100 |  |  | OPPOSITE DRIVE END: | M9-90 INS
[6 empty] | BREAK DOWN (%): | 250
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.4 | [5 empty] | FULL LOAD: | 93.6
|  | 3/4 LOAD: | 95.1 | [5 empty] | 3/4 LOAD: | 93
|  | 1/2 LOAD: | 94.1 | [5 empty] | 1/2 LOAD: | 90.5
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Mario L
[9 empty] | DATE: | 2014-10-22
- | M9-90 INS |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS