## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | Z:\Motor R&D\Active Projects\6810 Development\Electrical Design\TEAAC\4P\Series\BS4M25U.rat |  |  |  |  | Date: | 2014-12-11 | Time: | 8:36
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
4 | 1250 | 1800 | FCW4 | 4000 | 60 | 105 | 1788.9 / 1784.7 | 0.0062 / 0.0085 | 6810US
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 23.1256 | LR Test Data
Air Gap | 3.31 | [5 empty] | Rt. Slot Pitch | 28.3491 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 16 | Cross Section Area |  | Mean Value | 25.7373 | 754.0139
Core Length | 590 | 590 |  |  | UB: 420.0 | UER: 3750.0 | Eff.T.W.St. | 15.4098 | WS
OD | 815 | 523.38 | Coil Pitch | 0.83325 |  |  | Eff.T.W.Rt. | 27.2462 | 32017.9519
ID | 530 | 300 | Slot Fill | - | EBL: 50.5 | ERD1: 423.4 | St.Carter Fac. | 1.5007 | IS
Core Depth | 66.5 | 71.14 | Con./Slot | 18 |  | ERT: 75.00 | Rt.Carter Fac. | 1.0405 | 157.033
Eff.Core L. | 442.68 | 442.68 | Wire Size 1 | (.114"x.204")x1 | (12 x 35) | ERH: 50.00 | Carter Factor | 1.5614 | Volts / Turn
Slot Data |  |  | Wire Size 2 | (.114"x.229")x1 |  |  | Short. Factor | 0.96589 | 21.384
Number | 72 | 58 | // Circuits | 2 |  |  | Distrib. Factor | 0.95597 | AC
Kind | Open | Rectang | Connection | Wye |  |  | Wind. Factor | 0.92336 | 611.1399
Skew | - | 0 | MCL | 1311 | 766 |  | Reactance | (Coeff.: 0.0486)
Depth | 76 | 40.55 | No.Cond./Ph. | 216 |  |  |  | Running | Start
Width | 15.20 - 15.20 | 12.05 | Res. (20°C) | 0.080216 |  |  | Stator Slot | 14.7605 | 14.7605
Opening | 15.2 | 5 | (105°C) | 0.10701 | 0.088703 | 0.013634 | Rotor Slot | 20.2716 | 14.8241
Tip Depth | 3.65 | 5.5 | Material | CU | CU | CU | Zigzag | 4.4184 | 4.1797
T.Min.Wid. | 7.9256 | 11.9122 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 19.5093 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 3.2736 | 3.1388
Up. R. | - | 0.8 | Weight (kg) |  |  |  | Total Resist. | 0.20934 | 0.4328
Wedge Dep. | 1.20 - 0.50 | Normal | Wire 1 | 218.3289 | 182.1273 | 99.9842 | Total React. | 3.0231 | 2.7383
Duct | 19 x 6 | 19 x 6 | Wire 2 | 246.1019 | - | - | Impedance | 3.0304 | 2.7723
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.0017 |  | Length | Section | Density | AT | Volume | Loss
| Reac.= | 35.0362 | Primary Core | 32.0049 | 588.7644 | 14.7652 | 342.8755 | 69223.3878 | 4617.2756
Excitation Data |  |  | Tooth | 7.6 | 631.5303 | 13.7654 | 66.2379 | 19198.5209 | 1143.0558
Excit.Amps | 44.970 / 39.455 |  | Second.Core | 17.3683 | 629.8451 | 13.8022 | 152.6752 | Total | 5760.3314
Core Loss | 1.885 / 1.653 | Flux / Pole | Tooth | 4.055 | 764.628 | 11.3692 | 19.1134 | C.L.C. | 1.75 / 0.77
NoLoad | 45.01 / 39.49 | 8.6932 | Air Gap | 0.331 | 1268.95 | 6.8507 | 1804.4948 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 37 / 37 |  | No Load Loss | 22556.7 / 15584.5 | W.Loss | 10080.6 / 4441.2
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 7916.2 / 7230.0 | S.Loss | 2989.4 / 1317.1
Current (A) | 61.25 / 61.80 | 88.43 / 89.21 | 121.31 / 122.38 | 157.03 / 158.43 | 194.93 / 196.66 | Second. Loss | 5981.6 / 8047.6 | Total C.Loss | 13070.0 / 5758.3
Efficiency | 0.908 / 0.901 | 0.947 / 0.940 | 0.959 / 0.952 | 0.963 / 0.956 | 0.965 / 0.957 | Frict.& Wind. | 9000.0 / 10095.0 | Stray Loss | 11492.5225
P.F. | 0.605 / 0.604 | 0.803 / 0.802 | 0.868 / 0.866 | 0.890 / 0.888 | 0.895 / 0.893 | Starting Data |  | Slip | PF
Slip | 0.0016 / 0.0039 | 0.0031 / 0.0054 | 0.0046 / 0.0069 | 0.0062 / 0.0085 | 0.0078 / 0.0101 | LRA | 833.1 / 882.5
RPM | 1797.2 / 1793.0 | 1794.5 / 1790.3 | 1791.7 / 1787.5 | 1788.9 / 1784.7 | 1786.0 / 1781.8 | % | 530.5 / 562.0
L (Inv., MH) | 6.298 | 6.298 | 6.298 | 6.298 | 6.298 | LRT (kg.m) | 367.8 / 380.9 |  | 0.15612
(No Load) | 6.298 |  | Correlated to: P148750_TestData_lab1457.dat |  |  | % | 72.4 / 75.0
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 2406.2521 | 0.03383 | 0.63247
IM/IW | 0.32217 | I*R1/E | 0.0072185 | Rosenberg | 826.6001 | % | 256.4 / 239.7
IW*X/E | 0.18272 | I*R2/E | 0.0061852 | Schwisky | 1174.3474 | Amps | 530.5429
SUM | 0.50489 | Friction/OP. | 0.0096515 | Tsurumi | 762.8181 | Max. Output | 2326.2718 | 0.032667 | 0.64421
IH/I | 0.012097 | Total | 0.035152 | Thrust (1mm) | 305.1007 | % | 249.4661
|  | Efficiency | 0.96485 | Thrust (3 mm) | 767.8757 | Amps | 521.1908
Single Cage Data | [5 empty] | Miscellaneous Data
Slot Number | 58 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.044914 | Coil Cur. Density
Depth | 40.55 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 130389.0733 | 2.55 / 2.58
Opening | 5 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 135.7247 | Bar Cur. Den.
Tip Depth | 5.5 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 316171.1 | UB: 3.43 / 3.46 | LB: -
Up. Sl. Wid. | 12.05 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.87494 | UER: 1.78 / 1.79 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.28487 | 0.68737 | 75.7685 | 548.3746
0.002 | 126.6813 | 138.6613 | 0.79158 | 75.3563 | 552.5448
0.01 | 235 | 406.1503 | 0.89579 | 75.1242 | 555.9793
0.062105 | 131.0702 | 473.8798 | 1 | 75 | 558.8608
0.11421 | 102.9793 | 493.821
0.16632 | 90.6661 | 504.2653 | Acceleration Data (FV V)
0.27053 | 83.0666 | 518.0836 | Load Type: | Fan / Pump
0.37474 | 79.6156 | 528.4822 | Load Inertia: | 686.6 kg.m²
0.47895 | 77.6539 | 536.6951 | Accel. Time: | 14.4 (s)
0.58316 | 76.4751 | 543.2202 | Rated Torque: | 507.7 kg.m
Load
100
99.6
98
83.8526
70.3053
57.4105
38.0105
24.7789
15.6842
9.0105
6.2526
7.8316
14.7053
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | BS4M25U | [5 empty] | HRW / Model Number: | M255TCQL11F-C
Type: TIKE - Form: FCW4 - 4 Pole - 1250 HP - 4000 V - 60 Hz - 6810US - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M36 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 3.31 |  | No load amps |  |  |  | 40 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 590 |  | No load watts |  |  |  | 16238 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 9 |  | Impedance amps |  | 3 | f | 248 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.114"x.204")x1 |  | Impedance volts |  | 3 | f | 1150 | - |  | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | (.114"x.229")x1 |  | Impedance watts |  | 3 | f | 66973 | - |  | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 2 x Wye |  |  | Winding |  | 80/115 | 37 / 49 | -
MCL |  | 1311 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 16.6292 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.8018 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 18 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 158 |  | 1027
Coil grouping |  | - |  |  |  | RPM |  | 1785
Coil pitch (slot number) |  | 1 ~ 16 |  |  |  | CODE |  | E
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.08025 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 500 |  |  |  | Nom.Eff. (%): |  |  |  |  | Adjacent
(lbs.) | Wire2 | 561 |  |  |  | Min.Eff. (%): |  |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 258 / 1442 | 346 / 179
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 883 | - | 558.8608
[6 empty] | LRT (%) | 60 | 75 | -
[6 empty] | BDT (%) | 175 | 239 | -
[6 empty] | SLIP (%) |  | 0.85 | -
[5 empty] | IEEE-B | Eff. (%) |  | 95.5 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 88.8 | -
|  |  |  | Losses (Watts) |  | Primary |  | 7230 | -
[6 empty] | Secondary |  | 8048 | -
[6 empty] | Core |  | 5758 | -
[6 empty] | F & W(Sleeve Brg) |  | 10768 | -
[6 empty] | Stray |  | 11493 | -
End Ring (Reference) |  |  |  | Note
Outer Fan: T530
Limits: BS4M25U
Approved |  | Design | Mario L
Date |  | Date | 2014-12-11 |  | Rev 0: First Issue
40.55
5.50
5.00
12.05
76.0
3.65
15.2
423.4
50.5
75.0
50.0
051-TB23
411-TB23
311-TB23
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## Form
Winding Data Calculation
MCL: 1311.0
Coil Resistance |  |  | Lead Resistance
9T: | 0.0135 ~ 0.0130 |  | AWG. (02 x 2) x 3
0.00092
Coil Dimensions
HM: | 9T: 27.86 | WM: | 9T: 11.40 | WT:
15.30 ~ 14.90
Insulation Allowance |  |  | Wire Weight
Depth: | 16.63 |  | (.114"x.204")x 1: |  | 500 lbs.
Width: | 3.80 |  | (.114"x.229")x 1: |  | 561 lbs.
QC Resistance
1-2, 2-3, 3-1: |  | 0.165 ~ 0.156

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | M255TCQL11F-C |  |  | FLAmps: | 158
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 6810US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1250 | Rotor Inertia: | 805.2 lb-ft² | Date: | 2014-12-11
FLRPM: | 1785 | Load Inertia: | N/A | File: | BS4M25U
| Locked Rotor Amps: | 883 A | Load Type: | N/A
| Locked Rotor Torque: | 75% | Starting at: | N/A
| Breakdown Torque: | 235% | Accel. Time: | N/A
| Rated Torque: | 3678 lb-ft
Comments: |  |  |  | D.E.Curve #: | BS4M25U
|  | Prepared by: | Mario L | Checked by:
100 | 0 | 0.28487
99.8 | 126.6813 | 138.6613
99 | 235 | 406.1503
93.7895 | 131.0702 | 473.8798
88.5789 | 102.9793 | 493.821
83.3684 | 90.6661 | 504.2653
72.9474 | 83.0666 | 518.0836
62.5263 | 79.6156 | 528.4822
52.1053 | 77.6539 | 536.6951
41.6842 | 76.4751 | 543.2202
31.2632 | 75.7685 | 548.3746
20.8421 | 75.3563 | 552.5448
10.4211 | 75.1242 | 555.9793
0 | 75 | 558.8608

## StallTime
Rating: | 4 Pole - 1250.0 HP - 1800 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 4073.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~188 | 75.1 | 22.4 | 1.537 | 880.7 | 384.8 | 1024.8
188~375 | 75.2 | 11.3 | 1.266 | 875.7 | 313.6 | 757.2
375~563 | 75.6 | 7.0 | 1.183 | 869.7 | 289.4 | 627.1
563~750 | 76.1 | 7.6 | 1.183 | 862.4 | 285.0 | 547.5
750~938 | 77.1 | 12.3 | 1.252 | 853.1 | 296.1 | 496.4
938~1125 | 78.6 | 20.2 | 1.387 | 841.5 | 320.2 | 458.6
1125~1313 | 81.3 | 31.4 | 1.623 | 826.8 | 363.4 | 430.6
1313~1501 | 86.9 | 47.7 | 2.067 | 807.7 | 444.5 | 412.8
1501~1594 | 96.8 | 63.9 | 1.227 | 788.5 | 250.1 | 329.1
1594~1688 | 117.0 | 77.1 | 1.015 | 764.5 | 198.4 | 212.3
1688~1782 | 183.0 | 90.9 | 0.440 | 695.2 | 79.1 | 63.6
1782~1796 | 180.8 | 98.8 | 0.076 | 430.4 | 10.0 | 20.6
1796~1800 | 113.3 | 99.8 | 0.115 | 145.1 | 0.9 | 41.8
Acceleration Time: 14.4 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 3236 kW / s |  | 18°C |  | 36°C
Rotor Bar Rise | 4700 kW / s |  | 67°C |  | 134°C
End Ring Rise | 722 kW / s |  | 19°C |  | 38°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 1.5°C / s |  | 261.9 kW | 160°C | 109.3 s
Rotor Bar | 8.6°C / s |  | 606.2 kW | 260°C | 30.1 s
Rotor ER | 2.4°C / s |  | 93.2 kW | 180°C | 74.4 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 37°C + |  | 123°C + | 40°C | = 200°C | 84.0 s
Rotor Bar | 45°C + |  | 215°C + | 40°C | = 300°C | 24.9 s
Rotor ER | 45°C + |  | 135°C + | 40°C | = 220°C | 55.8 s
Cold Stall Time: | 64.7 s |  | Hot Stall Time: |  | 48.5 s

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | M255TCQL11F-C |  |  | FLAmps: | 158
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 6810US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1250 | Rotor Inertia: | 805.2 lb-ft² | Date: | 2014-12-11
FLRPM: | 1785 | Load Inertia: | 4073.0 lb-ft² | File: | BS4M25U
Comments: |  |  |  | D.E.Curve #: | BS4M25U
|  | Prepared by: | Mario L | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
558.8608 | 35 | 15 |  | 558.8608 | 0.0001
492.5805 | 45.0527 | 19.3083 |  | 557.4051 | 1.537
426.2803 | 60.1568 | 25.7815 |  | 554.2405 | 2.803
360 | 84.3471 | 36.1488 |  | 550.443 | 3.986
260 | 161.7069 |  |  | 545.8228 | 5.169
160 | 427.0073 |  |  | 539.9367 | 6.421
235 | 197.9427 | 84.8326 |  | 532.5949 | 7.808
180 | 434.2933 | 144.5951 |  | 523.2911 | 9.431
145 | 519.9233 | 222.8243 |  | 511.2025 | 11.498
125 |  | 500 |  | 499.0506 | 12.725
125 |  | 1000 |  | 483.8608 | 13.74
125 |  | 10000 |  | 440 | 14.18
|  |  |  | 272.4051 | 14.256
|  |  |  | 0 | 14.371

## MagNoise
Magnetic Noise Verification
Rating: | 4 Pole - 1250.0 HP - 1800 RPM - 4000 V - 60 Hz
Electromagnetic Excitation Frequencies
| L = | 0 | L = | + 1 | L = | - 1 | Slip = | 0 | Slip = | 0.006
Mode A | 10 |  | 22 |  | 2 |  | 1860.0 Hz |  | 1849.2 Hz
Mode B | 18 |  | 30 |  | 6 |  | 1620.0 Hz |  | 1609.2 Hz
Mode C | 14 |  | 26 |  | 2 |  | 1740.0 Hz |  | 1729.2 Hz
Natural Frequencies of Stator Core
| Mode 0 = |  | 1283.2 Hz |  | Mode 6 = |  | 2255.8 Hz
| Mode 2 = |  | 175.3 Hz |  | Mode 7 = |  | 3104.8 Hz
| Mode 3 = |  | 495.9 Hz |  | Mode 8 = |  | 4084.6 Hz
| Mode 4 = |  | 950.8 Hz |  | Mode 9 = |  | 5195.2 Hz
| Mode 5 = |  | 1537.7 Hz |  | Mode 10 = |  | 6436.5 Hz
Analysis Results
No matching frequencies detected.

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | M255TCQL11F-C |  |  | FLAmps: | 158
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 6810US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1250 | Rotor Inertia: | 805.2 lb-ft² | Date: | 2014-12-11
FLRPM: | 1785 | Load Inertia: | 4073.0 lb-ft² | File: | BS4M25U
| Locked Rotor Amps: | 883 A | Load Type: | N/A
| Locked Rotor Torque: | 75% | Starting at: | N/A
| Breakdown Torque: | 235% | Accel. Time: | N/A
| Rated Torque: | 3678 lb-ft
Comments: |  |  |  | D.E.Curve #: | BS4M25U
|  | Prepared by: | Mario L | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 45.4107 | 100 | 0.40595
25 | 90.1403 | 60.3628 | 61.7977 | 64.7622 | 6.4608
50 | 94.0523 | 80.144 | 89.2175 | 51.2403 | 12.3842
75 | 95.2211 | 86.5591 | 122.3872 | 37.4081 | 18.3483
100 | 95.5 | 88.756 | 158.4331 | 23.3339 | 24.3552
125 | 95.6 | 89.2657 | 196.6693 | 8.8548 | 30.4067
1800
1798
1796
1794
1792
1790
1788
1786
1784
1782
1780
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 11/08/96
[9 empty] | SUPERSEDES |  | 10/06/95
[9 empty] | REVISION |  | 1
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | R. EVANS
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | Jay Bugbee
CUSTOMER:
TIC SR No.:
MOTOR NAMEPLATE DATA
| H.P.: | 1250 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1800
| FRAME: | 6810US |  | ENCL: | TEAAC |  | FLAMPS: | 158 |  |  | FLRPM: | 1785
| FORM: | FCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | E |  |  | DUTY: | Cont.
| MODEL No.: | M255TCQL11F-C |  |  |  |  | kW:
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 883 |  |  | FULL LOAD (lb-ft.): | 3678 |  |  | DRIVE END: | M11-125 INS
[6 empty] | LOCKED ROTOR (%): | 75 |  |  | OPPOSITE DRIVE END: | M11-125 INS
[6 empty] | BREAK DOWN (%): | 235
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.5 | [5 empty] | FULL LOAD: | 88.8
|  | 3/4 LOAD: | 95.2 | [5 empty] | 3/4 LOAD: | 86.6
|  | 1/2 LOAD: | 94 | [5 empty] | 1/2 LOAD: | 80.2
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Mario L
[9 empty] | DATE: | 2014-12-11
- | M11-125 INS |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS