## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | Z:\Motor R&D\Active Projects\6810 Development\Electrical Design\TEAAC\6P\Series\BS6M35U.rat |  |  |  |  | Date: | 2014-12-19 | Time: | 16:11
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
6 | 1750 | 1200 | FCCW4 | 4000 | 60 | 105 | 1192.2 / 1192.3 | 0.0065 / 0.0064 | 6813US
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.6528 | LR Test Data
Air Gap | 2.1 | [5 empty] | Rt. Slot Pitch | 30.3759 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 11 | Cross Section Area |  | Mean Value | 27.5143 | 660.5353
Core Length | 924 | 924 |  |  | UB: 420.0 | UER: 1500.0 | Eff.T.W.St. | 15.4159 | WS
OD | 815 | 560.8 | Coil Pitch | 0.83325 |  |  | Eff.T.W.Rt. | 29.5367 | 48111.0276
ID | 565 | 300 | Slot Fill | - | EBL: 50.5 | ERD1: 460.8 | St.Carter Fac. | 1.2038 | IS
Core Depth | 63 | 93.85 | Con./Slot | 20 |  | ERT: 30.00 | Rt.Carter Fac. | 1.0284 | 215.7354
Eff.Core L. | 691.92 | 691.92 | Wire Size 1 | (.081"x.182")x2 | (12 x 35) | ERH: 50.00 | Carter Factor | 1.238 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.96589 | 28.8684
Number | 72 | 58 | // Circuits | 3 |  |  | Distrib. Factor | 0.95749 | AC
Kind | Open | Rectang | Connection | Wye |  |  | Wind. Factor | 0.92484 | 583.3975
Skew | - | 0 | MCL | 1459 | 1055 |  | Reactance | (Coeff.: 0.0417)
Depth | 62 | 36.55 | No.Cond./Ph. | 160 |  |  |  | Running | Start
Width | 9.24 - 9.24 | 12.05 | Res. (20°C) | 0.073654 |  |  | Stator Slot | 19.9906 | 19.9906
Opening | 13.2 | 3.5 | (105°C) | 0.098253 | 0.067248 | 0.009662 | Rotor Slot | 13.687 | 8.2395
Tip Depth | 2.83 | 1.5 | Material | CU | CU | CU | Zigzag | 6.9208 | 4.6303
T.Min.Wid. | 11.4528 | 14.3712 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 6.1745 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 3.8616 | 2.7706
Up. R. | - | 0.8 | Weight (kg) |  |  |  | Total Resist. | 0.17516 | 0.34457
Wedge Dep. | 2.83 - 3.20 | Magnetic | Wire 1 | 343.7384 | 234.968 | 43.7992 | Total React. | 2.1095 | 1.7339
Duct | 30 x 6 | 30 x 6 | Wire 2 | - | - | - | Impedance | 2.1167 | 1.7678
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.0017 |  | Length | Section | Density | AT | Volume | Loss
| Reac.= | 35.0362 | Primary Core | 21.3366 | 871.8192 | 13.4399 | 237.4561 | 102982.5803 | 5898.3465
Excitation Data |  |  | Tooth | 6.2 | 950.9268 | 12.3219 | 47.1174 | 35374.4771 | 1760.1475
Excit.Amps | 55.367 / 49.117 |  | Second.Core | 12.7679 | 1298.7338 | 9.022 | 40.125 | Total | 7658.494
Core Loss | 2.288 / 2.030 | Flux / Pole | Tooth | 3.655 | 961.226 | 12.1898 | 26.5349 | C.L.C. | 1.75 / 0.66
NoLoad | 55.41 / 49.16 | 11.7172 | Air Gap | 0.21 | 1777.8348 | 6.5907 | 1101.3908 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 69 / 70 |  | No Load Loss | 26662.1 / 18797.8 | W.Loss | 13402.4 / 5078.7
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 13718.6 / 12424.6 | S.Loss | 2466.4 / 934.6
Current (A) | 78.87 / 80.30 | 118.56 / 120.70 | 165.38 / 168.37 | 215.74 / 219.63 | 268.92 / 273.78 | Second. Loss | 8847.0 / 8709.1 | Total C.Loss | 15868.8 / 6013.3
Efficiency | 0.920 / 0.916 | 0.953 / 0.949 | 0.962 / 0.958 | 0.965 / 0.960 | 0.965 / 0.960 | Frict.& Wind. | 10116.0 / 9343.1 | Stray Loss | 17784.9121
P.F. | 0.649 / 0.641 | 0.834 / 0.823 | 0.888 / 0.877 | 0.905 / 0.894 | 0.908 / 0.896 | Starting Data |  | Slip | PF
Slip | 0.0016 / 0.0015 | 0.0032 / 0.0031 | 0.0049 / 0.0048 | 0.0065 / 0.0064 | 0.0082 / 0.0081 | LRA | 1306.4 / 1244.4
RPM | 1198.0 / 1198.1 | 1196.1 / 1196.2 | 1194.2 / 1194.3 | 1192.2 / 1192.3 | 1190.2 / 1190.3 | % | 605.6 / 576.8
L (Inv., MH) | 4.165 | 4.165 | 4.165 | 4.165 | 4.1483 | LRT (kg.m) | 1025.8 / 883.2 |  | 0.19492
(No Load) | 4.165 |  | Correlated to: P149087.dat |  |  | % | 96.2 / 82.8
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 3439.321 | 0.03642 | 0.63278
IM/IW | 0.28275 | I*R1/E | 0.0091437 | Rosenberg | 1274.7443 | % | 261.7 / 230.9
IW*X/E | 0.17886 | I*R2/E | 0.0065211 | Schwisky | 2284.1456 | Amps | 755.9187
SUM | 0.46161 | Friction/OP. | 0.0077488 | Tsurumi | 1871.3187 | Max. Output | 3316.4442 | 0.03506 | 0.64562
IH/I | 0.010646 | Total | 0.03406 | Thrust (1mm) | 565.5411 | % | 254.0363
|  | Efficiency | 0.96594 | Thrust (3 mm) | 1224.834 | Amps | 741.4201
Single Cage Data | [5 empty] | Miscellaneous Data
Slot Number | 58 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.08482 | Coil Cur. Density
Depth | 36.55 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 233985.5003 | 3.91 / 3.98
Opening | 3.5 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 264.9155 | Bar Cur. Den.
Tip Depth | 1.5 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 494183.4 | UB: 3.57 / 3.63 | LB: -
Up. Sl. Wid. | 12.05 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.87494 | UER: 3.09 / 3.14 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.25188 | 0.68737 | 80.9331 | 550.8764
0.002 | 107.9831 | 118.9745 | 0.79158 | 80.4384 | 556.6412
0.01 | 230 | 374.525 | 0.89579 | 80.1547 | 561.4214
0.062105 | 136.8687 | 452.0735 | 1 | 80 | 565.4545
0.11421 | 109.2947 | 476.8588
0.16632 | 96.7342 | 490.3087 | Acceleration Data (FV V)
0.27053 | 88.9021 | 508.6767 | Load Type: | Fan / Pump
0.37474 | 85.2336 | 522.8049 | Load Inertia: | 2537.8 kg.m²
0.47895 | 83.0828 | 534.2289 | Accel. Time: | 14.3 (s)
0.58316 | 81.7543 | 543.5278 | Rated Torque: | 1066.6 kg.m
Load
100
99.6
98
83.8526
70.3053
57.4105
38.0105
24.7789
15.6842
9.0105
6.2526
7.8316
14.7053
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | BS6M35U | [5 empty] | HRW / Model Number: | M357TCQL11E-C
Type: TIKE - Form: FCW4 - 6 Pole - 1750 HP - 4000 V - 60 Hz - 6813US - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M36 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 2.1 |  | No load amps |  |  |  | 49 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 924 |  | No load watts |  |  |  | 15880 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 10 |  | Impedance amps |  | 3 | f | 339 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.081"x.182")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 104531 | - |  | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 3 x Wye |  |  | Winding |  | 80/115 | 70 / 91 | -
MCL |  | 1459 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 14.022 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.5544 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 20 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 220 |  | 1430
Coil grouping |  | - |  |  |  | RPM |  | 1192
Coil pitch (slot number) |  | 1 ~ 11 |  |  |  | CODE |  | E
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.07275 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 783 |  |  |  | Nom.Eff. (%): |  |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 398 / 2251 | 363 / 314
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 1244 | - | 565.4545
[6 empty] | LRT (%) | 60 | 82 | -
[6 empty] | BDT (%) | 175 | 230 | -
[6 empty] | SLIP (%) |  | 0.64 | -
[5 empty] | IEEE-B | Eff. (%) |  | 96 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 89.4 | -
|  |  |  | Losses (Watts) |  | Primary |  | 12425 | -
[6 empty] | Secondary |  | 8709 | -
[6 empty] | Core |  | 6013 | -
[6 empty] | F & W |  | 9343 | -
[6 empty] | Stray |  | 17785 | -
End Ring (Reference) |  |  |  | Note
Outer Fan: 550OD
Limits: BS6M35U
Approved |  | Design | Mario L
Date |  | Date | 2014-12-19 |  | Rev 0: First Issue
36.55
1.50
3.50
12.05
62.0
2.83
13.2
051-TB31
460.8
50.5
30.0
50.0
411-TB31
311-TB31
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## Form
Winding Data Calculation
MCL: 1459.0
Coil Resistance |  |  | Lead Resistance
10T: | 0.0276 ~ 0.0265 |  | AWG. 3/0 x 3
0.00075
Coil Dimensions
HM: | 10T: 22.57 | WM: | 10T: 9.65 | WT:
13.30 ~ 12.90
Insulation Allowance |  |  | Wire Weight
Depth: | 14.02 |  | (.081"x.182")x 2: |  | 783 lbs.
Width: | 3.55
QC Resistance
1-2, 2-3, 3-1: |  | 0.150 ~ 0.141

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | M357TCQL11E-C |  |  | FLAmps: | 220
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 6813US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 1571.6 lb-ft² | Date: | 2014-12-19
FLRPM: | 1192 | Load Inertia: | N/A | File: | BS6M35U
| Locked Rotor Amps: | 1244 A | Load Type: | N/A
| Locked Rotor Torque: | 80% | Starting at: | N/A
| Breakdown Torque: | 230% | Accel. Time: | N/A
| Rated Torque: | 7711 lb-ft
Comments: |  |  |  | D.E.Curve #: | BS6M35U
|  | Prepared by: | Mario L | Checked by:
100 | 0 | 0.25188
99.8 | 107.9831 | 118.9745
99 | 230 | 374.525
93.7895 | 136.8687 | 452.0735
88.5789 | 109.2947 | 476.8588
83.3684 | 96.7342 | 490.3087
72.9474 | 88.9021 | 508.6767
62.5263 | 85.2336 | 522.8049
52.1053 | 83.0828 | 534.2289
41.6842 | 81.7543 | 543.5278
31.2632 | 80.9331 | 550.8764
20.8421 | 80.4384 | 556.6412
10.4211 | 80.1547 | 561.4214
0 | 80 | 565.4545

## StallTime
Rating: | 6 Pole - 1750.0 HP - 1200 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 15055.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~125 | 80.1 | 22.4 | 1.519 | 1239.6 | 692.7 | 1420.9
125~250 | 80.3 | 11.3 | 1.270 | 1229.9 | 571.1 | 1066.4
250~375 | 80.7 | 7.0 | 1.191 | 1218.3 | 526.3 | 886.6
375~500 | 81.3 | 7.6 | 1.189 | 1203.8 | 514.7 | 773.6
500~625 | 82.4 | 12.3 | 1.250 | 1185.5 | 526.8 | 697.0
625~750 | 84.2 | 20.2 | 1.371 | 1162.7 | 558.3 | 638.2
750~875 | 87.1 | 31.4 | 1.573 | 1134.6 | 613.4 | 587.7
875~1000 | 92.8 | 47.7 | 1.943 | 1098.9 | 717.2 | 546.5
1000~1063 | 103.0 | 63.9 | 1.118 | 1063.9 | 383.3 | 420.6
1063~1125 | 123.1 | 77.1 | 0.952 | 1021.8 | 309.0 | 278.1
1125~1188 | 183.4 | 90.9 | 0.474 | 909.3 | 138.1 | 94.2
1188~1198 | 169.0 | 98.8 | 0.096 | 542.8 | 19.2 | 33.6
1198~1200 | 104.0 | 99.8 | 0.400 | 191.8 | 5.7 | 171.8
Acceleration Time: 14.3 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 5576 kW / s |  | 42°C |  | 84°C
Rotor Bar Rise | 6659 kW / s |  | 74°C |  | 147°C
End Ring Rise | 957 kW / s |  | 57°C |  | 113°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 4.0°C / s |  | 535.3 kW | 160°C | 39.6 s
Rotor Bar | 10.1°C / s |  | 913.2 kW | 260°C | 25.8 s
Rotor ER | 7.8°C / s |  | 131.2 kW | 180°C | 23.1 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 70°C + |  | 90°C + | 40°C | = 200°C | 22.3 s
Rotor Bar | 94°C + |  | 166°C + | 40°C | = 300°C | 16.5 s
Rotor ER | 94°C + |  | 86°C + | 40°C | = 220°C | 11.1 s
Cold Stall Time: | 45.8 s |  | Hot Stall Time: |  | 22.0 s

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | M357TCQL11E-C |  |  | FLAmps: | 220
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 6813US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 1571.6 lb-ft² | Date: | 2014-12-19
FLRPM: | 1192 | Load Inertia: | 15055.0 lb-ft² | File: | BS6M35U
Comments: |  |  |  | D.E.Curve #: | BS6M35U
|  | Prepared by: | Mario L | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
565.4545 | 35 | 15 |  | 565.4545 | 0.0001
494.3101 | 45.7999 | 19.6285 |  | 563.4545 | 1.519
423.1444 | 62.5009 | 26.7861 |  | 559.0455 | 2.789
352 | 90.3188 | 38.7081 |  | 553.7727 | 3.98
252 | 176.2229 |  |  | 547.1818 | 5.169
152 | 484.3689 |  |  | 538.8636 | 6.419
230 | 211.5474 | 90.6632 |  | 528.5 | 7.79
180 | 451.9754 | 148.0272 |  | 515.7273 | 9.363
145 | 532.2644 | 228.1133 |  | 499.5 | 11.306
125 |  | 500 |  | 483.5909 | 12.424
125 |  | 1000 |  | 464.4545 | 13.376
125 |  | 10000 |  | 413.3182 | 13.85
|  |  |  | 246.7273 | 13.946
|  |  |  | 0 | 14.346

## MagNoise
Magnetic Noise Verification
Rating: | 6 Pole - 1750.0 HP - 1200 RPM - 4000 V - 60 Hz
Electromagnetic Excitation Frequencies
| L = | 0 | L = | + 1 | L = | - 1 | Slip = | 0 | Slip = | 0.007
Mode A | 8 |  | 26 |  | 10 |  | 1280.0 Hz |  | 1272.4 Hz
Mode B | 20 |  | 38 |  | 2 |  | 1040.0 Hz |  | 1032.4 Hz
Mode C | 14 |  | 32 |  | 4 |  | 1160.0 Hz |  | 1152.4 Hz
Natural Frequencies of Stator Core
| Mode 0 = |  | 1849.2 Hz |  | Mode 6 = |  | 3065.4 Hz
| Mode 2 = |  | 238.2 Hz |  | Mode 7 = |  | 4219.1 Hz
| Mode 3 = |  | 673.9 Hz |  | Mode 8 = |  | 5550.6 Hz
| Mode 4 = |  | 1292.1 Hz |  | Mode 9 = |  | 7059.8 Hz
| Mode 5 = |  | 2089.6 Hz |  | Mode 10 = |  | 8746.6 Hz
Analysis Results
Matching frequencies detected!!!
Please check slot combination!!!

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | M357TCQL11E-C |  |  | FLAmps: | 220
Enclosure: | TEAAC | Voltage: | 4000 V | Frame: | 6813US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 1571.6 lb-ft² | Date: | 2014-12-19
FLRPM: | 1192 | Load Inertia: | N/A | File: | BS6M35U
| Locked Rotor Amps: | 1244 A | Load Type: | N/A
| Locked Rotor Torque: | 80% | Starting at: | N/A
| Breakdown Torque: | 230% | Accel. Time: | N/A
| Rated Torque: | 7711 lb-ft
Comments: |  |  |  | D.E.Curve #: | BS6M35U
|  | Prepared by: | Mario L | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 56.413 | 100 | 0.397
25 | 91.5417 | 64.1161 | 80.2947 | 90.6777 | 8.9167
50 | 94.8265 | 82.3541 | 120.6947 | 81.138 | 17.2156
75 | 95.722 | 87.7278 | 168.3625 | 71.3825 | 25.5817
100 | 95.9762 | 89.4308 | 219.6253 | 61.3739 | 34.0187
125 | 95.9634 | 89.6909 | 273.7722 | 51.3183 | 42.529
1200
1198
1196
1194
1192
1190
1188
1186
1184
1182
1180
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 11/08/96
[9 empty] | SUPERSEDES |  | 10/06/95
[9 empty] | REVISION |  | 1
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | R. EVANS
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | Jay Bugbee
CUSTOMER:
TIC SR No.:
MOTOR NAMEPLATE DATA
| H.P.: | 1750 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1200
| FRAME: | 6813US |  | ENCL: | TEAAC |  | FLAMPS: | 220 |  |  | FLRPM: | 1192
| FORM: | FCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | E |  |  | DUTY: | Cont.
| MODEL No.: | M357TCQL11E-C |  |  |  |  | kW:
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 1244 |  |  | FULL LOAD (lb-ft.): | 7711 |  |  | DRIVE END: | M11-125 INS
[6 empty] | LOCKED ROTOR (%): | 80 |  |  | OPPOSITE DRIVE END: | M11-125 INS
[6 empty] | BREAK DOWN (%): | 230
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 96 | [5 empty] | FULL LOAD: | 89.4
|  | 3/4 LOAD: | 95.8 | [5 empty] | 3/4 LOAD: | 87.7
|  | 1/2 LOAD: | 94.9 | [5 empty] | 1/2 LOAD: | 82.3
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Mario L
[9 empty] | DATE: | 2014-12-19
- | M11-125 INS |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS