## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-1-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RATFILE\RF2400.rat |  |  |  |  | Date: | 2018-09-07 | Time: | 8:08
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 400 | 3600 | FCKW | 4000 | 60 | 105 | 3581.3 / 3576.4 | 0.0052 / 0.0066 | 5011
Core Data |  |  | Winding Data | USA Wire Std |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 23.9359 | LR Test Data
Air Gap | 2.5 | [5 empty] | Rt. Slot Pitch | 29.1059 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 14 | Cross Section Area |  | Mean Value | 26.5209 | 706.8391
Core Length | 500 | 500 |  |  | UB: 452.3 | UER: 2340.0 | Eff.T.W.St. | 14.2492 | WS
OD | 550 | 315 | Coil Pitch | 0.61899 |  | ERT: 45.0 | Eff.T.W.Rt. | 29.1059 | 15500.0839
ID | 320 | 135 | Slot Fill | - |  | ERD1: 205.0 | St.Carter Fac. | 1.2045 | IS
Core Depth | 59 | 46.7 | Con./Slot | 18 |  | ERD2: 315.0 | Rt.Carter Fac. | 1 | 50.6979
Eff.Core L. | 465 | 465 | Wire Size 1 | (.081"x.204")x2 |  |  | Carter Factor | 1.2045 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.82618 | 18.3291
Number | 42 | 34 | // Circuits | 1 |  |  | Distrib. Factor | 0.95565 | AC
Kind | Open | Dbl - Closed | Connection | Wye |  |  | Wind. Factor | 0.78954 | 381.2521
Skew | - | 0 | MCL | 1097 | 545 |  | Reactance | (Coeff.: 0.0923)
Depth | 56 | 43.3 | No.Cond./Ph. | 252 |  |  |  | Running | Start
Width | 9.69 - 9.69 |  | Res. (20°C) | 0.2326 |  |  | Stator Slot | 17.7572 | 17.7572
Opening | 14 | 0 | (105°C) | 0.31029 | 0.1834 | 0.08266 | Rotor Slot | 61.2951 | 37.1785
Tip Depth | 2.83 | 0.8 | Material | CU | AL | AL | Zigzag | 5.6206 | 5.5191
T.Min.Wid. | 12.7284 | 10 | Spec.Resist. | 1.742 | 3.25 | 3.25 | Coil End | 15.6303 | Skew R.: 0.00
Low. R. | 0 | 1.5 | Spec.Gravity | 8.89 | 2.67 | 2.67 | Belt Leakage | 7.4035 | 7.3477
Up. R. | - | 1.5 | Weight (kg) |  |  |  | Total Resist. | 0.57635 | 2.0102
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 152.6397 | 20.5296 | 10.6345 | Total React. | 9.9443 | 7.6959
Duct | - | - | Wire 2 | - | - | - | Impedance | 9.961 | 7.9541
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 42.4631 |  | Length | Section | Density | AT | Volume | Loss |  | 3571.6 | 125RPM
| Reac.= | 42.4895 | Primary Core | 43.1969 | 548.7 | 15.8818 | 499.1765 | 42319.0551 | 3176.5506 |  | 3576.4 | 100RPM
Excitation Data |  |  | Tooth | 5.6 | 1242.9327 | 7.0111 | 4.4318 | 13920.8458 | 277.8452 |  | 3581.1 | 75RPM
Excit.Amps | 13.265 / 12.706 |  | Second.Core | 17.9385 | 800.4975 | 10.8861 | 55.4572 | Total | 3454.3958 |  | 3585.7 | 50RPM
Core Loss | 0.965 / 0.925 | Flux / Pole | Tooth | 4.33 | 790.5 | 11.0238 | 13.8897 | C.L.C. | 1.75 / 0.73 |  | 3590.2 | 25RPM
NoLoad | 13.30 / 12.74 | 8.7143 | Air Gap | 0.25 | 2086.5248 | 4.1765 | 830.8844 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 78 / 78 |  | No Load Loss | 12318.0 / 8503.0 | W.Loss | 6045.2 / 2532.3
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 2392.6 / 2614.7 | S.Loss | 650.1 / 272.3
Current (A) | 19.67 / 20.20 | 28.66 / 29.43 | 39.28 / 40.34 | 50.70 / 52.06 | 62.73 / 64.42 | Second. Loss | 1628.8 / 2090.8 | Total C.Loss | 6695.3 / 2804.6
Efficiency | 0.855 / 0.850 | 0.918 / 0.912 | 0.939 / 0.934 | 0.949 / 0.943 | 0.954 / 0.948 | Frict.& Wind. | 5500.0 / 5885.4 | Stray Loss | 4545.3999 | 0.949 | 0.943 | 0.99368 | Eff.
P.F. | 0.640 / 0.627 | 0.819 / 0.802 | 0.875 / 0.858 | 0.8953 / 0.8770 | 0.900 / 0.882 | Starting Data |  | Slip | PF | 0.8953 | 0.8770 | 0.97956 | PF.
Slip | 0.0014 / 0.0027 | 0.0026 / 0.0040 | 0.0039 / 0.0052 | 0.0052 / 0.0066 | 0.0065 / 0.0079 | LRA | 290.3 / 340.0 |  |  | 50.70 | 52.06 | 1.0268 | Current
RPM | 3595.1 / 3590.2 | 3590.6 / 3585.7 | 3586.0 / 3581.1 | 3581.3 / 3576.4 | 3576.4 / 3571.6 | % | 572.7 / 670.6 |  |  | 3581.3 | 3575 | 0.99824 | RPM
L (Inv., MH) | 17.532 | 15.3466 | 14.2283 | 13.5772 | 13.1512 | LRT (kg.m) | 116.6 / 150.5 |  | 0.25273
(No Load) | 25.8851 |  | Correlated to: RF2400.dat |  |  | % | 143.6 / 185.5
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 735.913 | 0.026742 | 0.63955
IM/IW | 0.29364 | I*R1/E | 0.0067748 | Rosenberg | 194.8402 | % | 245.3 / 237.5
IW*X/E | 0.19451 | I*R2/E | 0.0052043 | Schwisky | 358.8323 | Amps | 161.638 |  |  | HP0.95 | 296.4538
SUM | 0.48815 | Friction/OP. | 0.018432 | Tsurumi | 151.0768 | Max. Output | 716.504 | 0.026016 | 0.64879 | HP1.5 | 8000
IH/I | 0.019145 | Total | 0.049556 | Thrust (1mm) | 4.3472 | % | 240.1153 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.95044 | Thrust (3 mm) | 10.0424 | Amps | 159.3974 |  |  | (RPM/1000)1.8 | 10.031
Double Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 34 | Slit Width | 3 | T.M.Wid.Low. | 10 | Watt Rad. | 0.036234 | Coil Cur. Density |  | k | 0.0685
Depth | 43.3 | Slit Depth | 9.5 | Cal.T.W.Up. | 0 | DG2L(cm2) | 49612.5 | 2.45 / 2.51 |  | Hz | 60
Opening | 0 | L.S.Up.Wid. | 16.6813 | Cal.M.T.Wid. | 0 | GD2L(kg.m2) | 19.6912 | Bar Cur. Den. |  | Load Inertia | 315.3635
Tip Depth | 0.8 | L.S.Low.Wid. | 11.1215 | Cal.M.T.Wid. | 10 | DO2L(cm2) | 151250 | UB: 1.75 / 1.80 | LB: -
Up. Sl. Wid. | 3 | L.S.Depth | 30 | X2S | 0 | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | 1.5 | T.M.Wid.Up. | 25.4037 | X3S | 0 | Coil Pitch Ct. | 0.67848 | UER: 1.84 / 1.89 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.25577 | 0.7 | 153.7738 | 639.716
0.01 | 139.2841 | 173.2805 | 0.8 | 158.8723 | 645.559
0.05 | 235 | 489.894 | 0.9 | 168.2311 | 650.3881
0.1 | 177.8056 | 562.6968 | 1 | 185 | 653.8462
0.15 | 156.6978 | 583.0436
0.2 | 151.9087 | 593.1741 | Acceleration Data (FV V)
0.3 | 151.3239 | 605.9424 | Load Type: | Fan / Pump
0.4 | 150.7317 | 616.1025 | Load Inertia: | 53.1 kg.m²
0.5 | 150 | 624.8223 | Accel. Time: | 6.8 (s)
0.6 | 151.1266 | 632.7802 | Rated Torque: | 81.2 kg.m
DesPro8AX Draft
Load
100
98
87
74
61
50
33
22
14
8
6
8
15
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | RF2400 | [5 empty] | HRW / Model Number: | 4003FTAL11F-A
Type: TIKK - Form: FCKW - 2 Pole - 400 HP - 2300/4000 V - 60 Hz - 5011 - Class F | [10 empty] | TEST PREDICT | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST | DESPRO | QC LIMIT | EPACT | M22 - 26Ga.
Material |  | M36 - 26Ga. |  | NL & Impedance Test | [5 empty] | 2300V | 2300V | EQP-III | M36 - 26Ga.
Air Gap |  | 2.5 |  | No load amps |  |  |  | 12.7 | 13.4 | 22 | 23.2126 | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 500 |  | No load watts |  |  |  | 8503 | 11039 | 8470 | 10996.1578 | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 9 |  | Impedance amps |  | 3 | f | 82 | 76.3 | 99 | 92.1183 | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.081"x.204")x2 |  | Impedance volts |  | 3 | f | 1150 | 1150 | 460 | 460 | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 15500 | 39513 | 15611 | 39795.9641 | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 1 Delta / 1 x Wye |  |  | Winding |  | 80/115 | 78 / 103 | -
MCL |  | 1097 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 12.5368 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.2368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 18 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 90 / 52
Coil grouping |  | - |  |  |  | RPM |  | 3575
Coil pitch (slot number) |  | 1 ~ 14 |  |  |  | CODE |  | G
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.2326 |  |  |  | DESIGN |  | B |  |  |  | Skip
Coil Weight | Wire1 | 335.8 |  |  |  | Nom.Eff. (%): |  | - |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 251 / 1641 | 180 / 189
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | 334 | 589 / 340 | - | #VALUE!
[6 empty] | LRT (%) | 70 | 185 | -
[6 empty] | BDT (%) | 175 | 237 | -
[6 empty] | SLIP (%) |  | 0.66 | -
[5 empty] | IEEE-B | Eff. (%) |  | 94.3 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 87.7 | -
|  |  |  | Losses (Watts) |  | Primary |  | 2615 | -
[6 empty] | Secondary |  | 2091 | -
[6 empty] | Core |  | 2805 | -
[6 empty] | F & W |  | 5885 | -
[6 empty] | Stray |  | 4545 | -
End Ring (Reference) |  |  |  | Note | Outer Fan OD: 360T Unidirectional
361-V120-3L1Y, 361-V120-3L1D, 361-V120-6L1DY
362-V110-02
Rev.2 Complete Performance Data Sheet. Z.X 09/07/18
Rev.1 Design Temperature, Performance and
Approved | H. Yamaga | Design | A. Gracia |  | losses were corrected.
Date | 2007-06-25 | Date | 2007-04-23 |  | A. Gracia 05/14/10
56.0
2.83
14.0
2340.0
315.0
55.0
45.0
205.0
0.80
43.30
1.5
11.0
3.0
16.68
30.00
11.12
Section
mm2
Section
mm2
M
M
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 2 Pole - 400.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 315.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~360 | 176.6 | 22.5 | 0.559 | 339.1 | 60.1 | 333.8
360~720 | 163.6 | 11.5 | 0.566 | 336.9 | 60.3 | 276.8
720~1080 | 156.3 | 7.0 | 0.577 | 334.2 | 60.5 | 236.7
1080~1440 | 152.5 | 7.0 | 0.592 | 330.8 | 61.0 | 205.7
1440~1800 | 150.6 | 11.0 | 0.617 | 327.0 | 62.2 | 180.6
1800~2160 | 150.4 | 18.0 | 0.650 | 322.6 | 63.9 | 157.5
2160~2520 | 151.0 | 27.5 | 0.697 | 317.7 | 66.6 | 135.8
2520~2880 | 151.6 | 41.5 | 0.782 | 311.8 | 72.3 | 114.7
2880~3060 | 154.3 | 55.5 | 0.436 | 305.8 | 38.6 | 85.5
3060~3240 | 167.3 | 67.5 | 0.431 | 297.9 | 36.9 | 65.5
3240~3420 | 206.4 | 80.5 | 0.342 | 273.7 | 27.3 | 39.3
3420~3564 | 187.1 | 92.5 | 0.364 | 172.4 | 22.0 | 34.5
3564~3581 | 119.6 | 99.0 | 0.200 | 48.5 | 0.5 | 9.8
Acceleration Time: 6.8 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 632 kW / s |  | 11°C |  | 22°C
Rotor Bar Rise | 1293 kW / s |  | 70°C |  | 141°C
End Ring Rise | 583 kW / s |  | 61°C |  | 122°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 2.2°C / s |  | 129.6 kW | 160°C | 72.6 s
Rotor Bar | 20.7°C / s |  | 380.5 kW | 260°C | 12.6 s
Rotor ER | 18.0°C / s |  | 171.5 kW | 180°C | 10.0 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 78°C + |  | 82°C + | 40°C | = 200°C | 37.2 s
Rotor Bar | 106°C + |  | 154°C + | 40°C | = 300°C | 7.4 s
Rotor ER | 106°C + |  | 74°C + | 40°C | = 220°C | 4.1 s
Cold Stall Time: | 12.1 s |  | Hot Stall Time: |  | 5.0 s

## Form
Winding Data Calculation
MCL: 1097.0
Coil Resistance |  |  | Lead Resistance
9T: | 0.0172 ~ 0.0165 |  | AWG. 06 x 3
0.00090
Coil Dimensions
HM: | 9T: 20.32 | WM: | 9T: 10.76 | WT:
14.10 ~ 13.70
Insulation Allowance |  |  | Wire Weight
Depth: | 12.54 |  | (.081"x.204")x 2: |  | 347 lbs.
Width: | 3.24
QC Resistance
1-2, 2-3, 3-1: |  | 0.487 ~ 0.459

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | DYKMAN ELECTRICAL INC
| TIC SR No.: | 2103004.1
MOTOR NAMEPLATE DATA
| H.P.: | 400 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5011UZ |  | ENCL: | TEFC |  | FLAMPS: | 52 |  |  | FLRPM: | 3575
| FORM: | FCKW |  | S.F.: | 1.15 |  | NEMA DESIGN: | B |  |  | INSUL CLASS: | F
| TYPE: | TIKK |  | AMB.: | 40°C |  | CODE: | G |  |  | DUTY: | Cont.
| MODEL No.: | GP-10011492 |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 340 |  |  | FULL LOAD (lb-ft.): | 588 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 185 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 235
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 94.3 | [5 empty] | FULL LOAD: | 87.7
|  | 3/4 LOAD: | 93.3 | [5 empty] | 3/4 LOAD: | 85.8
|  | 1/2 LOAD: | 91.2 | [5 empty] | 1/2 LOAD: | 80.2
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2023-03-27
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | GP-10011492 |  |  | FLAmps: | 52 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5011UZ
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 400 | Rotor Inertia: | 116.8 lb-ft² | Date: | 2023-03-27
FLRPM: | 3575 | Load Inertia: | 315.0 lb-ft² | File: | RF2400
| Locked Rotor Amps: | 340 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 185% | Starting at: | FV (V)
| Breakdown Torque: | 235% | Accel. Time: | 6.8 (s)
| Rated Torque: | 588 lb-ft
Comments: | PROJECT | 2103004.1 |  | D.E.Curve #: | RF2400
|  | Prepared by: | Zichao Xie | Checked by:
Load
100 | 0 | 0.25577 | 100
99 | 139.2841 | 173.2805 | 98
95 | 235 | 489.894 | 87
90 | 177.8056 | 562.6968 | 74
85 | 156.6978 | 583.0436 | 61
80 | 151.9087 | 593.1741 | 50
70 | 151.3239 | 605.9424 | 33
60 | 150.7317 | 616.1025 | 22
50 | 150 | 624.8223 | 14
40 | 151.1266 | 632.7802 | 8
30 | 153.7738 | 639.716 | 6
20 | 158.8723 | 645.559 | 8
10 | 168.2311 | 650.3881 | 15
0 | 185 | 653.8462 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | GP-10011492 |  |  | FLAmps: | 52
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5011UZ
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 400 | Rotor Inertia: | 116.8 lb-ft² | Date: | 2023-03-27
FLRPM: | 3575 | Load Inertia: | 315.0 lb-ft² | File: | RF2400
340 A
185%
588 lb-ft
Comments: | PROJECT | 2103004.1 |  | D.E.Curve #: | RF2400
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
653.8462 | 17 | 7 |  | 653.8462 | 0.0001
600 | 20.1882 | 8.3128 |  | 652.1154 | 0.559
500 | 29.071 | 11.9704 |  | 647.8846 | 1.125
400 | 45.4234 | 18.7038 |  | 642.6923 | 1.702
300 | 80.7528 |  |  | 636.1538 | 2.294
200 | 181.6938 |  |  | 628.8462 | 2.911
235 | 131.6026 | 54.1893 |  | 620.3846 | 3.561
180 | 266.3813 | 92.3643 |  | 610.9615 | 4.258
145 | 345.6719 | 142.3355 |  | 599.6154 | 5.04
125 |  | 300 |  | 588.0769 | 5.476
125 |  | 600 |  | 572.8846 | 5.907
125 |  | 10000 |  | 526.3462 | 6.249
|  |  |  | 235 | 6.613
|  |  |  | 125 | 6.813

## Performance 4000V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | GP-10011492 |  |  | FLAmps: | 52 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5011UZ
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 400 | Rotor Inertia: | 116.8 lb-ft² | Date: | 2023-03-27
FLRPM: | 3575 | Load Inertia: | 315.0 lb-ft² | File: | RF2400
| Locked Rotor Amps: | 340 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 185% | Starting at: | FV (V)
| Breakdown Torque: | 235% | Accel. Time: | 6.8 (s)
| Rated Torque: | 588 lb-ft
Comments: | PROJECT | 2103004.1 |  | D.E.Curve #: | RF2400
|  | Prepared by: | Zichao Xie | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 13.6563 | 100 | 1.5308
25 | 84.95 | 62.7191 | 20.1989 | 71.6023 | 10.971
50 | 91.2101 | 80.1835 | 29.4302 | 60.3556 | 20.436
75 | 93.3332 | 85.7588 | 40.3364 | 48.8558 | 29.9567
100 | 94.2921 | 87.7001 | 52.0566 | 37.0459 | 39.5361
125 | 94.753 | 88.1659 | 64.4121 | 25.0294 | 49.1797
3600
3596
3592
3588
3584
3580
3576
3572
3568
3564
3560
RPM
800
400
320
240
160
80
Input Watts (kW)
480
560
640
720
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance 2300v
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | GP-10011492 |  |  | FLAmps: | 90 A
Enclosure: | TEFC | Voltage: | 2300 V | Frame: | 5011UZ
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 400 | Rotor Inertia: | 116.8 lb-ft² | Date: | 2023-03-27
FLRPM: | 3575 | Load Inertia: | 315.0 lb-ft² | File: | RF2400
| Locked Rotor Amps: | 589 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 185% | Starting at: | FV (V)
| Breakdown Torque: | 235% | Accel. Time: | 6.8 (s)
| Rated Torque: | 588 lb-ft
Comments: | PROJECT | 2103004.1 |  | D.E.Curve #: | RF2400
|  | Prepared by: | Zichao Xie | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 23.6535 | 100 | 1.5308
25 | 84.95 | 62.7191 | 34.9856 | 71.6023 | 10.971
50 | 91.2101 | 80.1835 | 50.9746 | 60.3556 | 20.436
75 | 93.3332 | 85.7588 | 69.8648 | 48.8558 | 29.9567
100 | 94.2921 | 87.7001 | 90 | 37.0459 | 39.5361
125 | 94.753 | 88.1659 | 111.565 | 25.0294 | 49.1797
3600
3596
3592
3588
3584
3580
3576
3572
3568
3564
3560
RPM
800
400
320
240
160
80
Input Watts (kW)
480
560
640
720
EFF.
P.F.
RPM
AMPS
WATTS
0

## Rev. 1
TOSHIBA INTERNATIONAL CORPORATION | [6 empty] | INDEX | MPCF-1109
Industrial Division / Houston Motor Plant | [6 empty] | SHEET NO. | 1 of 1
[7 empty] | ISSUED | 2004-11-18
EQUIVALENT CIRCUIT DATA | [6 empty] | SUPERSEDES | NEW
[7 empty] | REVISION | REV. 0
[7 empty] | WRITTEN BY | MDC
All Values are Presented in Ohms/Phase, Equivalent Wye Connection. | [6 empty] | APPROVED BY | Paul Anderson
| CUSTOMER: | DYKMAN ELECTRICAL INC
| TIC SR No.: | 2103004.1
MOTOR NAMEPLATE DATA
| H.P.: | 400 | VOLTS: | 4000 | 3 PH / | 60 Hz |  | S. RPM: | 3600
| FRAME: | 5011UZ | ENCL: | TEFC | FLAMPS: | 52 |  | FLRPM: | 3575
| FORM: | FCKW | S.F.: | 1.15 | NEMA DESIGN: | B |  | INSUL CLASS: | F
| TYPE: | TIKK | AMB.: | 40°C | CODE: | G |  | DUTY: | Cont.
| MODEL No.: | GP-10011492 |  |  | kW: | -
| NOM. EFF.: | - | MIN. EFF.: | - | P.F.: | -
Primary Resistance (R1) : |  |  |  | 0.310
Secondary Resistance (R2) : |  |  |  | 0.266
Starting Resistance (R3) : |  |  |  | 1.70
Primary Reactance (X1) : |  |  |  | 3.31
Secondary Reactance (X2) : |  |  |  | 6.96
Starting Reactance (X3) : |  |  |  | 4.57
Magnetizing Reactance (Xm) : |  |  |  | 181.8
Transient Reactance : |  |  |  | 10.1
Sub Transient Reactance : |  |  |  | 6.03
Short Circuit Time Constant : |  |  |  | 0.102
Sub Transient Time Constant : |  |  |  | 0.011
Open Circuit Time Constant : |  |  |  | 1.88
[6 empty] | CERTIFIED BY: | JERRY R
[6 empty] | DATE: | 2023-03-27

## PERFORMANCE SPEC
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1082
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 2/14/02
[9 empty] | SUPERSEDES |  | NEW
[9 empty] | REVISION |  | 0
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | M. CAMPBELL
API 541 PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | P.A.A
| CUSTOMER: | DYKMAN ELECTRICAL INC
| TIC SR No.: | 2103004.1
MOTOR NAMEPLATE DATA
| H.P.: | 400 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5011UZ |  | ENCL: | TEFC |  | FLAMPS: | 52 |  |  | FLRPM: | 3575
| FORM: | FCKW |  | S.F.: | 1.15 |  | NEMA DESIGN: | B |  |  | INSUL CLASS: | F
| TYPE: | TIKK |  | AMB.: | 40°C |  | CODE: | G |  |  | DUTY: | Cont.
| MODEL No.: | GP-10011492 |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
LOCKED ROTOR DATA
|  |  | AMPS AT RATED VOLTAGE: | 340 |  |  |  | POWER FACTOR: | 26.8
|  |  | AMPS AT 80% VOLTAGE: | 272
TORQUE VALUES | [6 empty] | CURVE NUMBERS
|  |  |  | FULL LOAD (LB.FT): | 588 |  |  |  | SPEED-TORQUE CURVE: | RF2400
|  |  |  | LOCKED ROTOR TORQUE (% OF FLT): | 185 |  |  |  | SPEED-CURRENT CURVE: | RF2400
|  |  |  | PULL UP TORQUE (% OF FLT): | 150 |  |  |  | ACCELERATION CURVE: | RF2400
|  |  |  | BREAKDOWN TORQUE (% OF FLT): | 235
LOCKED ROTOR WITHSTAND TIMES
COLD CONDITION | [6 empty] | HOT CONDITION
|  | 100% VOLTAGE: | 17 | [5 empty] | 100% VOLTAGE: | 7
|  | 90% VOLTAGE: | 21 | [5 empty] | 90% VOLTAGE: | 9
|  | 80% VOLTAGE: | 27 | [5 empty] | 80% VOLTAGE: | 11
|  | 70% VOLTAGE: | 35 | [5 empty] | 70% VOLTAGE: | 14
DESIGN DATA
|  | MOTOR ROTOR wk2 (LB.FT2): | 116.8 | [5 empty] | NO LOAD CURRENT: | 13
|  | AIR GAP: | 2.5 | [5 empty] | ACCELERATION TIME: | 7/11
LOAD CHARACTERISTICS
|  |  | LOAD |  |  | 1/2 | 3/4 | FULL | 1.15
|  |  | AMPS (A) |  |  | 29.4 | 40.3 | 52
|  |  | EFFICIENCY (%) |  |  | 91.2 | 93.4 | 94.3
|  |  | POWER FACTOR (%) |  |  | 80.2 | 85.8 | 87.4
|  |  | GUARENTEED EFFICIENCY (%) |  |  | - | - | - | -
EFFICIENCY TO BE DETERMINED BY IEEE 112, METHOD B
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2023-03-27
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE, FREQUENCY AND SINEWAVE POWER INPUT.