## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RAT FILES\CS4800.rat |  |  |  |  | Date: | 2020-02-03 | Time: | 9:16
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
4 | 800 | 1800 | FCW4 | 4000 | 60 | 115 | 1788.0 / 1789.0 | 0.0067 / 0.0061 | 5811US
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 20.9963 | LR Test Data
Air Gap | 2.3 | [5 empty] | Rt. Slot Pitch | 24.9065 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 14 | Cross Section Area |  | Mean Value | 22.9514 | 849.4873
Core Length | 760 | 760 |  |  | UB: 350.0 | UER: 1978.0 | Eff.T.W.St. | 12.1013 | WS
OD | 610 | 396.4 | Coil Pitch | 0.86658 |  |  | Eff.T.W.Rt. | 24.3245 | 22118.195 |  |  |  |  | 6.0375
ID | 401 | 155 | Slot Fill | - | EBL: 63.5 | ERD1: 308.4 | St.Carter Fac. | 1.2154 | IS
Core Depth | 51.5 | 80.65 | Con./Slot | 21 |  | ERT: 46.00 | Rt.Carter Fac. | 1.0239 | 98.5743
Eff.Core L. | 706.8 | 706.8 | Wire Size 1 | (.064"x.182")x2 | (10 x 35) | ERH: 43.00 | Carter Factor | 1.2445 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.97812 | 21.9949
Number | 60 | 50 | // Circuits | 2 |  |  | Distrib. Factor | 0.95651 | AC
Kind | Open | Rectang | Connection | Wye |  |  | Wind. Factor | 0.93558 | 492.9586
Skew | - | 0 | MCL | 1265 | 933 |  | Reactance | (Coeff.: 0.0905)
Depth | 53 | 40.05 | No.Cond./Ph. | 210 |  |  |  | Running | Start
Width | 8.89 - 8.89 | 10.05 | Res. (20°C) | 0.16055 |  |  | Stator Slot | 18.4319 | 18.4319
Opening | 13 | 3 | (115°C) | 0.22048 | 0.14914 | 0.01892 | Rotor Slot | 26.7931 | 20.531
Tip Depth | 2.83 | 5 | Material | CU | Special | Special | Zigzag | 4.5228 | 4.2829
T.Min.Wid. | 7.9963 | 9.8305 | Spec.Resist. | 1.742 | 1.724 | 1.724 | Coil End | 7.2307 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 4.084 | 3.932
Up. R. | - | 0.8 | Weight (kg) |  |  |  | Total Resist. | 0.38855 | 0.75875
Wedge Dep. | 2.80 - 2.00 | Magnetic | Wire 1 | 204.209 | 152.3079 | 38.8193 | Total React. | 5.5253 | 4.9174
Duct | - | - | Wire 2 | - | - | - | Impedance | 5.539 | 4.9756
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.0038 |  | Length | Section | Density | AT | Volume | Loss |  | 1785.9 | 125RPM
| Reac.= | 35.0368 | Primary Core | 23.9546 | 728.004 | 12.122 | 138.5842 | 63866.9896 | 3094.7996 |  | 1789.0 | 100RPM
Excitation Data |  |  | Tooth | 5.3 | 847.767 | 10.4096 | 19.047 | 17972.6599 | 680.4829 |  | 1792.2 | 75RPM
Excit.Amps | 19.805 / 22.048 |  | Second.Core | 12.4211 | 1140.0684 | 7.7407 | 24.0011 | Total | 3775.2825 |  | 1795.1 | 50RPM
Core Loss | 1.067 / 1.188 | Flux / Pole | Tooth | 4.005 | 868.5208 | 10.1608 | 13.4112 | C.L.C. | 1.75 / 0.69 |  | 1798.0 | 25RPM
NoLoad | 19.83 / 22.08 | 8.8249 | Air Gap | 0.23 | 1923.2973 | 4.5884 | 839.81 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 74 / 74 |  | No Load Loss | 16889.1 / 11580.0 | W.Loss | 6606.7 / 2590.1
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 6427.2 / 6166.9 | S.Loss | 793.4 / 311.0
Current (A) | 32.62 / 33.05 | 52.37 / 53.06 | 74.72 / 75.70 | 98.57 / 99.87 | 123.99 / 125.62 | Second. Loss | 4217.5 / 3779.9 | Total C.Loss | 7400.2 / 2901.1
Efficiency | 0.894 / 0.893 | 0.939 / 0.937 | 0.952 / 0.950 | 0.957 / 0.955 | 0.958 / 0.956 | Frict.& Wind. | 9300.0 / 8444.6 | Stray Loss | 6731.6001 | 0.957 | 0.955 | 0.99791 | Eff.
P.F. | 0.738 / 0.730 | 0.876 / 0.866 | 0.908 / 0.898 | 0.913 / 0.903 | 0.907 / 0.896 | Starting Data |  | Slip | PF | 0.913 | 0.903 | 0.98905 | PF.
Slip | 0.0017 / 0.0011 | 0.0033 / 0.0027 | 0.0049 / 0.0044 | 0.0067 / 0.0061 | 0.0084 / 0.0078 | LRA | 464.2 / 675.9 |  |  | 98.57 | 99.87 | 1.0132 | Current
RPM | 1797.0 / 1798.0 | 1794.1 / 1795.1 | 1791.2 / 1792.2 | 1788.0 / 1789.0 | 1784.9 / 1785.9 | % | 470.9 / 685.7 |  |  | 1788.0 | 1789.0 | 1.0006 | RPM
L (Inv., MH) | 11.7811 | 11.7811 | 11.7811 | 11.7811 | 11.7811 | LRT (kg.m) | 188.6 / 261.4 |  | 0.1525
(No Load) | 11.7811 |  | Correlated to: CS4800_EXP2_Fan550_Lab324.dat |  |  | % | 58.0 / 80.4
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1326.1885 | 0.030392 | 0.64086
IM/IW | 0.21654 | I*R1/E | 0.0094604 | Rosenberg | 447.942 | % | 220.7 / 234.3
IW*X/E | 0.21882 | I*R2/E | 0.0066556 | Schwisky | 798.4536 | Amps | 289.6026 |  |  | HP0.95 | 572.7109
SUM | 0.43535 | Friction/OP. | 0.015583 | Tsurumi | 650.73 | Max. Output | 1286.5184 | 0.029448 | 0.65153 | HP1.5 | 22627.4163
IH/I | 0.010768 | Total | 0.042467 | Thrust (1mm) | 6.3096 | % | 215.5694 |  |  | (RPM/1000)2.4 | 4.0988
|  | Efficiency | 0.95753 | Thrust (3 mm) | 14.1363 | Amps | 285.0001 |  |  | (RPM/1000)1.8 | 2.8807
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 24
Slot Number | 50 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.060873 | Coil Cur. Density |  | k | 0.0685
Depth | 40.05 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 119421.0497 | 3.42 / 3.46 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 71.3069 | Bar Cur. Den. |  | Load Inertia | 2815.3914
Tip Depth | 5 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 282796 | UB: 3.08 / 3.12 | LB: -
Up. Sl. Wid. | 10.05 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.89993 | UER: 2.17 / 2.20 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.19833 | 0.68737 | 80.5721 | 661.3412
0.002 | 139.7313 | 178.5898 | 0.79158 | 80.2649 | 667.1481
0.01 | 230 | 497.5158 | 0.89579 | 80.0919 | 671.9531
0.062105 | 128.4679 | 569.4587 | 1 | 80 | 676
0.11421 | 102.7479 | 590.9631
0.16632 | 92.1568 | 603.0109 | Acceleration Data (FV V)
0.27053 | 85.9719 | 620.292 | Load Type: | Fan / Pump
0.37474 | 83.3904 | 634.0142 | Load Inertia: | 474.6 kg.m²
0.47895 | 81.9599 | 645.1915 | Accel. Time: | 14.1 (s)
0.58316 | 81.0943 | 654.1374 | Rated Torque: | 325.1 kg.m
Load
100
99.6
98
83.8526
70.3053
57.4105
38.0105
24.7789
15.6842
9.0105
6.2526
7.8316
14.7053
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | CS4800 | [5 empty] | HRW / Model Number: | 8004FTQL11E-C
Type: TIKE - Form: FCW4 - 4 Pole - 800 HP - 4000 V - 60 Hz - 5811US - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M36 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 2.3 |  | No load amps |  |  |  | 22 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 760 |  | No load watts |  |  |  | 11580 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 10.5 |  | Impedance amps |  | 3 | f | 133 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.064"x.182")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 22118 | - |  | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [6 empty] | Dry Kiln
Connection |  | 2 x Wye |  |  | Winding |  | 80/115 | 74 / 98 | -
MCL |  | 1265 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 11.8324 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.3544 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 21 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 100 |  | 650
Coil grouping |  | - |  |  |  | RPM |  | 1785
Coil pitch (slot number) |  | 1 ~ 14 |  |  |  | CODE |  | G
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.1606 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 449.3 |  |  |  | Nom.Eff. (%): |  |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%):
FL / LR |  | 346 / 2339 | 312 / 220
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 676 | - | 676
[6 empty] | LRT (%) | 60 | 80 | -
[6 empty] | BDT (%) | 175 | 234 | -
[6 empty] | SLIP (%) |  | 0.61 | -
[5 empty] | IEEE-B | Eff. (%) |  | 95.5 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 90.3 | -
|  |  |  | Losses (Watts) |  | Primary |  | 6167 | -
[6 empty] | Secondary |  | 3780 | -
[6 empty] | Core |  | 2901 | -
[6 empty] | F & W |  | 8445 | -
[6 empty] | Stray |  | 6732 | -
End Ring (Reference) |  |  |  | Note | TEFC-4P-800HP CuBar, Sleeve Brgs.
|  |  |  | LINK: | CS4800_EXP2.rat with CS4800_EXP2_Fan550_Lab324.dat
[5 empty] | QC Limits: CS4800 |  |  | Outer Fan OD: 550 mm
NEW ROTOR SLOT DIE
Rev.2 Updated Performance data per test report
Approved | S. Hernandez | Design | A. Gracia |  | Lab # 324 |  |  |  | A. Gracia 11/3/10
Date | 2009-12-21 | Date | 2009-11-10
Rev.1 The file ID was changed from CF to CS
[5 empty] | for sleeve bearing design. |  |  |  | A. Gracia 04/15/10
40.05
5.00
3.00
10.05
53.0
2.83
13.0
308.4
43.0
63.5
46.0
M
311-
411-
051-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 4 Pole - 800.0 HP - 1800 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 2815.4 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~188 | 80.0 | 22.4 | 1.456 | 674.0 | 440.0 | 643.2
188~375 | 80.2 | 11.3 | 1.219 | 669.6 | 364.1 | 483.1
375~563 | 80.4 | 7.0 | 1.144 | 664.2 | 336.9 | 401.6
563~750 | 80.8 | 7.6 | 1.147 | 657.7 | 332.0 | 351.0
750~938 | 81.5 | 12.3 | 1.214 | 649.7 | 343.5 | 317.0
938~1125 | 82.7 | 20.2 | 1.346 | 639.6 | 370.6 | 291.8
1125~1313 | 84.7 | 31.4 | 1.576 | 627.2 | 419.0 | 272.0
1313~1501 | 89.1 | 47.7 | 2.029 | 611.7 | 516.3 | 260.6
1501~1594 | 97.5 | 63.9 | 1.250 | 597.0 | 300.6 | 211.6
1594~1688 | 115.6 | 77.1 | 1.091 | 580.2 | 252.0 | 141.4
1688~1782 | 179.2 | 90.9 | 0.476 | 533.5 | 102.0 | 41.9
1782~1796 | 184.9 | 98.8 | 0.075 | 338.1 | 12.3 | 12.4
1796~1800 | 119.9 | 99.8 | 0.080 | 99.2 | 0.5 | 21.5
Acceleration Time: 14.1 s
| Energy |  | First Start |  | Second Start |  | Third Start
Stator Winding Rise | 3790 kW / s |  | 48°C |  | 96°C |  | 144°C
Rotor Bar Rise | 3061 kW / s |  | 52°C |  | 104°C |  | 156°C
End Ring Rise | 388 kW / s |  | 26°C |  | 52°C |  | 78°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 4.6°C / s |  | 359.3 kW | 160°C | 35.0 s
Rotor Bar | 7.2°C / s |  | 423.7 kW | 260°C | 36.0 s
Rotor ER | 3.6°C / s |  | 53.7 kW | 180°C | 50.1 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 74°C + |  | 86°C + | 40°C | = 200°C | 18.8 s
Rotor Bar | 100°C + |  | 160°C + | 40°C | = 300°C | 22.2 s
Rotor ER | 100°C + |  | 80°C + | 40°C | = 220°C | 22.3 s
Cold Stall Time: | 46.8 s |  | Hot Stall Time: |  | 20.8 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | JCI INDUSTRIES
| TIC SR No.: | 2210056.1
MOTOR NAMEPLATE DATA
| H.P.: | 800 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1800
| FRAME: | 5811UZ |  | ENCL: | TEFC |  | FLAMPS: | 100 |  |  | FLRPM: | 1785
| FORM: | FCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | G |  |  | DUTY: | Cont.
| MODEL No.: | GP-10035342 |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 676 |  |  | FULL LOAD (lb-ft.): | 2349 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 80 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 230
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.5 | [5 empty] | FULL LOAD: | 90.3
|  | 3/4 LOAD: | 95 | [5 empty] | 3/4 LOAD: | 89.8
|  | 1/2 LOAD: | 93.7 | [5 empty] | 1/2 LOAD: | 86.6
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2021-03-10
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS
Note on L22: Pick bearings from list!

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | GP-10035342 |  |  | FLAmps: | 100 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5811UZ
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 800 | Rotor Inertia: | 423.0 lb-ft² | Date: | 2021-03-10
FLRPM: | 1785 | Load Inertia: | 2815.4 lb-ft² | File: | CS4800
| Locked Rotor Amps: | 676 A | Load Type: | N/A
| Locked Rotor Torque: | 80% | Starting at: | N/A
| Breakdown Torque: | 230% | Accel. Time: | N/A
| Rated Torque: | 2349 lb-ft
Comments: | PROJECT | 2210056.1 |  | D.E.Curve #: | CS4800
|  | Prepared by: | JERRY R | Checked by:
Load
100 | 0 | 0.19833 | 100
99.8 | 139.7313 | 178.5898 | 99.6
99 | 230 | 497.5158 | 98
93.7895 | 128.4679 | 569.4587 | 83.8526
88.5789 | 102.7479 | 590.9631 | 70.3053
83.3684 | 92.1568 | 603.0109 | 57.4105
72.9474 | 85.9719 | 620.292 | 38.0105
62.5263 | 83.3904 | 634.0142 | 24.7789
52.1053 | 81.9599 | 645.1915 | 15.6842
41.6842 | 81.0943 | 654.1374 | 9.0105
31.2632 | 80.5721 | 661.3412 | 6.2526
20.8421 | 80.2649 | 667.1481 | 7.8316
10.4211 | 80.0919 | 671.9531 | 14.7053
0 | 80 | 676 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | GP-10035342 |  |  | FLAmps: | 100 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5811UZ
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 800 | Rotor Inertia: | 423.0 lb-ft² | Date: | 2021-03-10
FLRPM: | 1785 | Load Inertia: | 2815.4 lb-ft² | File: | CS4800
676 A
80%
2349 lb-ft
Comments: | PROJECT | 2210056.1 |  | D.E.Curve #: | CS4800
|  | Prepared by: | JERRY R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
676 | 35 | 15 |  | 676 | 0.0001
600 | 44.4282 | 19.0407 |  | 674 | 1.456
500 | 63.9766 | 27.4186 |  | 669.6 | 2.675
400 | 99.9635 | 42.8415 |  | 664.2 | 3.819
300 | 177.7129 |  |  | 657.7 | 4.966
200 | 399.854 |  |  | 649.7 | 6.18
230 | 302.3471 | 129.5773 |  | 639.6 | 7.526
180 | 626.6244 | 211.563 |  | 627.2 | 9.102
145 | 760.721 | 326.0233 |  | 611.7 | 11.131
125 |  | 700 |  | 597 | 12.381
125 |  | 1400 |  | 580.2 | 13.472
125 |  | 10000 |  | 533.5 | 13.948
|  |  |  | 230 | 14.023
|  |  |  | 125 | 14.103

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | GP-10035342 |  |  | FLAmps: | 100 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5811UZ
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 800 | Rotor Inertia: | 423.0 lb-ft² | Date: | 2021-03-10
FLRPM: | 1785 | Load Inertia: | 2815.4 lb-ft² | File: | CS4800
| Locked Rotor Amps: | 676 A | Load Type: | N/A
| Locked Rotor Torque: | 80% | Starting at: | N/A
| Breakdown Torque: | 230% | Accel. Time: | N/A
| Rated Torque: | 2349 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 1800 | 1600
[8 empty] | 1798 | 1440
Comments: | PROJECT | 2210056.1 |  | D.E.Curve #: | CS4800 |  |  | 1796 | 1280
[8 empty] | 1794 | 1120
[8 empty] | 1792 | 960
[8 empty] | 1790 | 800
|  | Prepared by: | JERRY R | Checked by: |  | SYNC SPEED | 1800 | 1788 | 640
[6 empty] | NEW SPEED LOWER RANGE | 1780 | 1786 | 480
[6 empty] | NEW kW UPPER RANGE | 1600 | 1784 | 320
[8 empty] | 1782 | 160
[8 empty] | 1780 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 22 | 100 | 0.72375
25 | 89.3 | 73 | 33.05 | 66.1532 | 10.4471
50 | 93.7 | 86.6 | 53.06 | 52.8995 | 19.8969
75 | 95 | 89.8 | 75.7 | 39.637 | 29.4356
100 | 95.5 | 90.3 | 99.87 | 25 | 39.0502
125 | 95.6 | 89.6 | 125.62 | 10.8235 | 48.738
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 20.0952 | 100 | 16.9238
25 | 89.2236 | 73.0104 | 33.0556 | 90.2568 | 10.45
50 | 93.6841 | 86.6294 | 53.0651 | 75.8925 | 19.905
75 | 95.0138 | 89.811 | 75.7033 | 61.2333 | 29.4396
100 | 95.4851 | 90.3181 | 99.8755 | 45.4631 | 39.0591
125 | 95.5911 | 89.656 | 125.6269 | 29.8532 | 48.7697
1800
1798
1796
1794
1792
1790
1788
1786
1784
1782
1780
RPM
1600
800
640
480
320
160
Input Watts (kW)
960
1120
1280
1440
EFF.
P.F.
RPM
AMPS
WATTS
0