## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RAT FILES\CF6400.rat |  |  |  |  | Date: | 2022-03-16 | Time: | 11:14
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
6 | 400 | 1200 | FCKW | 4000 | 60 | 105 | 1190.7 / 1178.8 | 0.0078 / 0.0177 | 5011
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 15.9261 | LR Test Data
Air Gap | 1.2 | [5 empty] | Rt. Slot Pitch | 19.6404 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 11 | Cross Section Area |  | Mean Value | 17.7832 | 699.3943
Core Length | 600 | 600 |  |  | UB: 240.0 | UER: 1596.0 | Eff.T.W.St. | 9.8881 | WS
OD | 550 | 362.6 | Coil Pitch | 0.83325 |  |  | Eff.T.W.Rt. | 18.6517 | 14130.0904
ID | 365 | 140 | Slot Fill | - | EBL: 63.5 | ERD1: 286.6 | St.Carter Fac. | 1.2251 | IS
Core Depth | 42.5 | 79.25 | Con./Slot | 14 |  | ERT: 42.00 | Rt.Carter Fac. | 1.053 | 51.2648
Eff.Core L. | 558 | 558 | Wire Size 1 | (.091"x.204")x1 | (8 x 30) | ERH: 38.00 | Carter Factor | 1.2901 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.96589 | 13.7468
Number | 72 | 58 | // Circuits | 1 |  |  | Distrib. Factor | 0.95749 | AC
Kind | Open | Rectang | Connection | Wye |  |  | Wind. Factor | 0.92484 | 450.6476
Skew | - | 0 | MCL | 939 | 769 |  | Reactance | (Coeff.: 0.1482)
Depth | 50 | 32.05 | No.Cond./Ph. | 336 |  |  |  | Running | Start
Width | 6.04 - 6.04 | 8.05 | Res. (20°C) | 0.47105 |  |  | Stator Slot | 25.8709 | 25.8709
Opening | 8.7 | 3 | (105°C) | 0.62838 | 0.37445 | 0.02558 | Rotor Slot | 18.718 | 12.5895
Tip Depth | 2.83 | 2 | Material | CU | Special | Special | Zigzag | 7.1298 | 5.3267
T.Min.Wid. | 7.2261 | 8.1223 | Spec.Resist. | 1.742 | 1.724 | 1.724 | Coil End | 4.8514 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 4.1895 | 3.3197
Up. R. | - | 0.8 | Weight (kg) |  |  |  | Total Resist. | 1.0284 | 1.7922
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 98.178 | 100.3603 | 29.2897 | Total React. | 9.0025 | 7.6703
Duct | - | - | Wire 2 | - | - | - | Impedance | 9.061 | 7.8769
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 30.0273 |  | Length | Section | Density | AT | Volume | Loss |  | 1176.4 | 125RPM |  | Kline/in2
| Reac.= | 30.0435 | Primary Core | 14.399 | 474.3 | 11.7639 | 90.3525 | 37810.1745 | 1745.2782 |  | 1178.8 | 100RPM |  | 75.8959
Excitation Data |  |  | Tooth | 5 | 483.8607 | 11.5314 | 29.0445 | 14515.8222 | 648.7191 |  | 1181.2 | 75RPM |  | 74.3962
Excit.Amps | 16.113 / 15.099 |  | Second.Core | 7.8147 | 884.43 | 6.3087 | 11.8408 | Total | 2393.9973 |  | 1183.5 | 50RPM |  | 40.7012
Core Loss | 0.727 / 0.682 | Flux / Pole | Tooth | 3.205 | 438.1145 | 12.7355 | 28.1056 | C.L.C. | 1.75 / 0.78 |  | 1185.7 | 25RPM |  | 82.1644
NoLoad | 16.13 / 15.11 | 5.5796 | Air Gap | 0.12 | 888.8594 | 6.2773 | 599.4355 | S.F.C. | 6.05 |  |  |  |  | 40.4984
Load Characteristics |  |  | Temp. Rise @ 100%: | 75 / 71 |  | No Load Loss | 7111.9 / 4351.2 | W.Loss | 4189.5 / 1870.8
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 4954.2 / 5153.6 | S.Loss | 855.5 / 382.0
Current (A) | 21.18 / 21.31 | 29.43 / 29.60 | 39.81 / 40.04 | 51.26 / 51.56 | 63.51 / 63.88 | Second. Loss | 2418.2 / 4047.2 | Total C.Loss | 5045.0 / 2252.8
Efficiency | 0.906 / 0.902 | 0.944 / 0.939 | 0.954 / 0.949 | 0.956 / 0.951 | 0.955 / 0.950 | Frict.& Wind. | 1700.0 / 1939.0 | Stray Loss | 2080.6379 | 0.956 | 0.951 | 0.99477 | Eff.
P.F. | 0.561 / 0.560 | 0.775 / 0.775 | 0.851 / 0.850 | 0.879 / 0.879 | 0.888 / 0.887 | Starting Data |  | Slip | PF | 0.879 | 0.879 | 1 | PF.
Slip | 0.0020 / 0.0119 | 0.0038 / 0.0138 | 0.0058 / 0.0157 | 0.0078 / 0.0177 | 0.0098 / 0.0197 | LRA | 293.2 / 346.2 |  |  | 51.26 | 51.56 | 1.0059 | Current
RPM | 1197.7 / 1185.7 | 1195.4 / 1183.5 | 1193.1 / 1181.2 | 1190.7 / 1178.8 | 1188.2 / 1176.4 | % | 571.9 / 675.3 |  |  | 1190.7 | 1178.8 | 0.99001 | RPM
L (Inv., MH) | 18.2759 | 18.2759 | 18.2759 | 18.2759 | 18.2759 | LRT (kg.m) | 244.1 / 300.1 |  | 0.22753
(No Load) | 18.2759 |  | Correlated to: CF6450_Fan550_H402115.dat |  |  | % | 100.0 / 123.0
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 777.5854 | 0.044328 | 0.613
IM/IW | 0.35895 | I*R1/E | 0.013811 | Rosenberg | 602.454 | % | 258.6 / 310.4
IW*X/E | 0.17498 | I*R2/E | 0.0077753 | Schwisky | 1035.9613 | Amps | 174.9694 |  |  | HP0.95 | 296.4538
SUM | 0.53393 | Friction/OP. | 0.0056971 | Tsurumi | 814.4913 | Max. Output | 743.931 | 0.042282 | 0.62867 | HP1.5 | 7999.9998
IH/I | 0.014331 | Total | 0.041614 | Thrust (1mm) | 9.1688 | % | 249.3066 |  |  | (RPM/1000)2.4 | 1.5489
|  | Efficiency | 0.95839 | Thrust (3 mm) | 15.7759 | Amps | 170.7947 |  |  | (RPM/1000)1.8 | 1.3884
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 24
Slot Number | 58 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.060973 | Coil Cur. Density |  | k | 0.0685
Depth | 32.05 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 78887.256 | 4.39 / 4.42 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 37.3392 | Bar Cur. Den. |  | Load Inertia | 4198.7007
Tip Depth | 2 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 181500 | UB: 3.01 / 3.02 | LB: -
Up. Sl. Wid. | 8.05 | L.S.Depth | - | X2S | - | IMC | 1.17 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.87494 | UER: 1.40 / 1.41 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.31018 | 0.69811 | 121.2953 | 645.1389
0.0088 | 124.7766 | 123.5442 | 0.79874 | 120.6289 | 653.0889
0.044 | 310 | 412.6481 | 0.89937 | 120.2269 | 659.7012
0.094316 | 226.6091 | 521.8642 | 1 | 120 | 665.3846
0.14463 | 173.6287 | 557.994
0.19495 | 148.563 | 575.7532 | Acceleration Data (FV V)
0.29558 | 133.0755 | 596.6337 | Load Type: | Fan / Pump
0.39621 | 127.0925 | 611.7976 | Load Inertia: | 707.8 kg.m²
0.49684 | 124.1096 | 624.6339 | Accel. Time: | 8.8 (s)
0.59747 | 122.3759 | 635.7851 | Rated Torque: | 244.1 kg.m
Load
100
98.24
88.65
75.4779
62.3958
51.1116
33.7516
22.4168
14.2526
8.1516
6.0379
7.9747
14.9558
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | CF6400 | [5 empty] | HRW / Model Number:
Type: TIKE - Form: FCKW - 6 Pole - 400 HP - 4000 V - 60 Hz - 5011 - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M36 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 1.2 |  | No load amps |  |  |  | 15.1 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 600 |  | No load watts |  |  |  | 4351 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 7 |  | Impedance amps |  | 3 | f | 84 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.091"x.204")x1 |  | Impedance volts |  | 3 | f | 1150 | - |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 14130 | - |  | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [6 empty] | Dry Kiln
Connection |  | 1 x Wye |  |  | Winding |  | 80/115 | 75 / 99 | -
MCL |  | 939 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 12.0104 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.3184 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 14 x 1 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 52 |  | 338
Coil grouping |  | - |  |  |  | RPM |  | 1180
Coil pitch (slot number) |  | 1 ~ 11 |  |  |  | CODE |  | G
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.471 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 216 |  |  |  | Nom.Eff. (%): |  | 95 |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | 87.5
FL / LR |  | 442 / 2941 | 302 / 141
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | 334 | 346 | - | 665.3846
[6 empty] | LRT (%) | 60 | 123 | -
[6 empty] | BDT (%) | 175 | 310 | -
[6 empty] | SLIP (%) |  | 1.77 | -
[5 empty] | IEEE-B | Eff. (%) |  | 95.1 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 87.9 | -
|  |  |  | Losses (Watts) |  | Primary |  | 5154 | -
[6 empty] | Secondary |  | 4047 | -
[6 empty] | Core |  | 2253 | -
[6 empty] | F & W |  | 1939 | -
[6 empty] | Stray |  | 2081 | -
End Ring (Reference) |  |  |  | Note
|  |  |  | LINK: | EXP_H402115.RAT & CF6450_FAN550_H402115.DAT
O-FAN AL/550/90/PLT 140-4614-01
RSO2: 400-V320-01 REF ONLY
USE MOTOR COVER &FAN COVER W/FOAM FOR 85dBA
Approved |  | Design | M.CAMPBELL
Date |  | Date | 2013-12-06 |  | BOM created from CF6400 EDS sheet, 350-H12011RU and 350-P143817U
32.05
2.00
3.00
8.05
50.0
2.83
8.7
286.6
38.0
63.5
42.0
311-
411-
051-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 6 Pole - 400.0 HP - 1200 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 4198.7 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~121 | 120.1 | 22.5 | 1.007 | 344.5 | 227.3 | 321.4
121~242 | 120.4 | 11.5 | 0.902 | 341.3 | 200.1 | 259.3
242~362 | 121.0 | 7.0 | 0.862 | 337.5 | 187.5 | 220.9
362~483 | 121.8 | 7.1 | 0.857 | 333.0 | 181.8 | 193.0
483~604 | 123.2 | 11.2 | 0.878 | 327.7 | 180.8 | 170.6
604~725 | 125.6 | 18.3 | 0.916 | 321.5 | 182.2 | 150.2
725~845 | 130.1 | 28.1 | 0.964 | 314.2 | 183.9 | 129.0
845~966 | 140.8 | 42.4 | 0.999 | 304.8 | 181.3 | 104.5
966~1026 | 161.1 | 56.8 | 0.471 | 294.8 | 79.6 | 72.6
1026~1087 | 200.1 | 68.9 | 0.375 | 280.8 | 59.5 | 50.0
1087~1147 | 268.3 | 82.1 | 0.264 | 243.0 | 36.6 | 30.0
1147~1189 | 217.4 | 93.4 | 0.278 | 139.4 | 24.1 | 28.8
1189~1191 | 112.4 | 99.1 | 0.075 | 36.3 | 0.4 | 19.1
Acceleration Time: 8.8 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 1725 kW / s |  | 46°C |  | 91°C
Rotor Bar Rise | 1638 kW / s |  | 42°C |  | 85°C
End Ring Rise | 112 kW / s |  | 10°C |  | 20°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 7.1°C / s |  | 269.2 kW | 160°C | 22.5 s
Rotor Bar | 8.7°C / s |  | 335.2 kW | 260°C | 30.0 s
Rotor ER | 2.0°C / s |  | 22.9 kW | 180°C | 88.7 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 75°C + |  | 85°C + | 40°C | = 200°C | 11.9 s
Rotor Bar | 101°C + |  | 159°C + | 40°C | = 300°C | 18.3 s
Rotor ER | 101°C + |  | 79°C + | 40°C | = 220°C | 38.7 s
Cold Stall Time: | 55.3 s |  | Hot Stall Time: |  | 24.1 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | -
| TIC SR No.: | -
MOTOR NAMEPLATE DATA
| H.P.: | 400 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1200
| FRAME: | 5011US |  | ENCL: | TEFC |  | FLAMPS: | 52 |  |  | FLRPM: | 1180
| FORM: | FCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | G |  |  | DUTY: | Cont.
| MODEL No.: | - |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 346 |  |  | FULL LOAD (lb-ft.): | 1782 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 120 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 310
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.1 | [5 empty] | FULL LOAD: | 87.9
|  | 3/4 LOAD: | 94.9 | [5 empty] | 3/4 LOAD: | 85.1
|  | 1/2 LOAD: | 93.9 | [5 empty] | 1/2 LOAD: | 77.5
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2022-03-16
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | - |  |  | FLAmps: | 52
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5011US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 400 | Rotor Inertia: | 221.5 lb-ft² | Date: | 2022-03-16
FLRPM: | 1180 | Load Inertia: | 4198.7 lb-ft² | File: | CF6400
| Locked Rotor Amps: | 346 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 120% | Starting at: | FV (V)
| Breakdown Torque: | 310% | Accel. Time: | 8.8 (s)
| Rated Torque: | 1782 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | CF6400
|  | Prepared by: | Zichao Xie | Checked by:
Load
100 | 0 | 0.31018 | 100
99.12 | 124.7766 | 123.5442 | 98.24
95.6 | 310 | 412.6481 | 88.65
90.5684 | 226.6091 | 521.8642 | 75.4779
85.5368 | 173.6287 | 557.994 | 62.3958
80.5053 | 148.563 | 575.7532 | 51.1116
70.4421 | 133.0755 | 596.6337 | 33.7516
60.3789 | 127.0925 | 611.7976 | 22.4168
50.3158 | 124.1096 | 624.6339 | 14.2526
40.2526 | 122.3759 | 635.7851 | 8.1516
30.1895 | 121.2953 | 645.1389 | 6.0379
20.1263 | 120.6289 | 653.0889 | 7.9747
10.0632 | 120.2269 | 659.7012 | 14.9558
0 | 120 | 665.3846 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | - |  |  | FLAmps: | 52
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5011US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 400 | Rotor Inertia: | 221.5 lb-ft² | Date: | 2022-03-16
FLRPM: | 1180 | Load Inertia: | 4198.7 lb-ft² | File: | CF6400
346 A
120%
1782 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | CF6400
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
665.3846 | 35 | 15 |  | 665.3846 | 0.0001
601.5961 | 42.8157 | 18.3496 |  | 662.5 | 1.007
537.7885 | 53.5785 | 22.9622 |  | 656.3462 | 1.909
474 | 68.9695 | 29.5583 |  | 649.0385 | 2.771
374 | 110.7823 |  |  | 640.3846 | 3.628
274 | 206.4013 |  |  | 630.1923 | 4.506
310 | 161.2465 | 69.1056 |  | 618.2692 | 5.422
180 | 585.0648 | 204.9707 |  | 604.2308 | 6.386
145 | 737.0171 | 315.8645 |  | 586.1538 | 7.385
125 |  | 700 |  | 566.9231 | 7.856
125 |  | 1400 |  | 540 | 8.231
125 |  | 10000 |  | 467.3077 | 8.495
|  |  |  | 268.0769 | 8.773
|  |  |  | 70.4034 | 8.848

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | - |  |  | FLAmps: | 52
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 5011US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 400 | Rotor Inertia: | 221.5 lb-ft² | Date: | 2022-03-16
FLRPM: | 1180 | Load Inertia: | 4198.7 lb-ft² | File: | CF6400
| Locked Rotor Amps: | 346 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 120% | Starting at: | FV (V)
| Breakdown Torque: | 310% | Accel. Time: | 8.8 (s)
| Rated Torque: | 1782 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 1200 | 800
[8 empty] | 1197 | 720
Comments: | PROJECT | - |  | D.E.Curve #: | CF6400 |  |  | 1194 | 640
[8 empty] | 1191 | 560
[8 empty] | 1188 | 480
[8 empty] | 1185 | 400
|  | Prepared by: | Zichao Xie | Checked by: |  | SYNC SPEED | 1200 | 1182 | 320
[6 empty] | NEW SPEED LOWER RANGE | 1170 | 1179 | 240
[6 empty] | NEW kW UPPER RANGE | 800 | 1176 | 160
[8 empty] | 1173 | 80
[8 empty] | 1170 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 15.1 | 100 | 0.54387
25 | 90.2 | 56 | 21.31 | 83.5124 | 10.3348
50 | 93.9 | 77.5 | 29.6 | 67.0256 | 19.8666
75 | 94.9 | 85 | 40.04 | 50.5375 | 29.4743
100 | 95.1 | 87.9 | 51.56 | 33.3333 | 39.2493
125 | 95 | 88.7 | 63.88 | 15.4122 | 49.0703
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 16.2246 | 100 | 7.1539
25 | 90.1659 | 56.0765 | 21.3093 | 52.2776 | 10.3483
50 | 93.9026 | 77.5147 | 29.6047 | 44.7639 | 19.8729
75 | 94.8591 | 85.0811 | 40.0499 | 37.0724 | 29.5088
100 | 95.0737 | 87.9058 | 51.5672 | 29.2097 | 39.2563
125 | 94.9649 | 88.7936 | 63.8877 | 21.115 | 49.1266
1200
1197
1194
1191
1188
1185
1182
1179
1176
1173
1170
RPM
800
400
320
240
160
80
Input Watts (kW)
480
560
640
720
EFF.
P.F.
RPM
AMPS
WATTS
0.0