## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | M:\Active Projects\6800 Frame TEFC\Electrical Design\6P\SERIES DESIGN\CS6M20U.rat |  |  |  |  | Date: | 2014-09-17 | Time: | 13:53
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
6 | 1000 | 1200 | FCW4 | 4000 | 60 | 105 | 1192.8 / 1191.4 | 0.0060 / 0.0072 | 6811US
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 23.1692 | LR Test Data
Air Gap | 2.1 | [5 empty] | Rt. Slot Pitch | 28.5343 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 11 | Cross Section Area |  | Mean Value | 25.8518 | 813.4161
Core Length | 910 | 910 |  |  | UB: 420.0 | UER: 1500.0 | Eff.T.W.St. | 13.502 | WS
OD | 770 | 526.8 | Coil Pitch | 0.83325 |  |  | Eff.T.W.Rt. | 27.6951 | 24138.1045
ID | 531 | 200 | Slot Fill | - | EBL: 50.5 | ERD1: 426.8 | St.Carter Fac. | 1.2384 | IS
Core Depth | 57.5 | 124.85 | Con./Slot | 17 |  | ERT: 30.00 | Rt.Carter Fac. | 1.0303 | 123.8734
Eff.Core L. | 846.3 | 846.3 | Wire Size 1 | (.102"x.204")x2 | (12 x 35) | ERH: 50.00 | Carter Factor | 1.2759 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.96589 | 22.6419
Number | 72 | 58 | // Circuits | 2 |  |  | Distrib. Factor | 0.95749 | AC
Kind | Open | Rectang | Connection | Wye |  |  | Wind. Factor | 0.92484 | 454.4493
Skew | - | 0 | MCL | 1457 | 1041 |  | Reactance | (Coeff.: 0.0828)
Depth | 62 | 38.55 | No.Cond./Ph. | 204 |  |  |  | Running | Start
Width | 9.67 - 9.67 | 12.05 | Res. (20°C) | 0.098695 |  |  | Stator Slot | 17.9946 | 17.9946
Opening | 14.2 | 3.5 | (105°C) | 0.13166 | 0.10705 | 0.014577 | Rotor Slot | 19.2907 | 13.8275
Tip Depth | 2.83 | 3.5 | Material | CU | Special | Special | Zigzag | 5.7038 | 5.1597
T.Min.Wid. | 8.9692 | 12.3139 | Spec.Resist. | 1.742 | 1.724 | 1.724 | Coil End | 5.1614 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 3.5215 | 3.2579
Up. R. | - | 0.8 | Weight (kg) |  |  |  | Total Resist. | 0.25328 | 0.52436
Wedge Dep. | 0.80 - 3.20 | Magnetic | Wire 1 | 415.8688 | 231.9362 | 40.6154 | Total React. | 4.2803 | 3.7549
Duct | - | - | Wire 2 | - | - | - | Impedance | 4.2878 | 3.7913
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.001 |  | Length | Section | Density | AT | Volume | Loss
| Reac.= | 35.036 | Primary Core | 20.1585 | 973.245 | 9.4426 | 70.429 | 108924.7455 | 3521.5791
Excitation Data |  |  | Tooth | 6.2 | 910.8788 | 10.0891 | 25.0804 | 33884.6909 | 1219.5741
Excit.Amps | 26.740 / 31.968 |  | Second.Core | 11.7731 | 2113.2111 | 4.3488 | 12.0859 | Total | 4741.1532
Core Loss | 1.376 / 1.646 | Flux / Pole | Tooth | 3.855 | 1007.3894 | 9.1225 | 12.4291 | C.L.C. | 1.75 / 0.84
NoLoad | 26.78 / 32.01 | 9.1899 | Air Gap | 0.21 | 1982.9895 | 4.6344 | 774.4658 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 71 / 76 |  | No Load Loss | 24758.0 / 8517.8 | W.Loss | 8297.0 / 4000.3
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 6060.7 / 5925.6 | S.Loss | 1249.3 / 602.3
Current (A) | 42.56 / 43.47 | 66.81 / 68.23 | 94.42 / 96.44 | 123.87 / 126.51 | 155.17 / 158.48 | Second. Loss | 4731.7 / 5162.5 | Total C.Loss | 9546.3 / 4602.6
Efficiency | 0.880 / 0.887 | 0.932 / 0.939 | 0.948 / 0.956 | 0.955 / 0.963 | 0.958 / 0.966 | Frict.& Wind. | 15000.0 / 5091.8 | Stray Loss | 7633.3296
P.F. | 0.719 / 0.698 | 0.865 / 0.840 | 0.902 / 0.876 | 0.910 / 0.883 | 0.905 / 0.879 | Starting Data |  | Slip | PF
Slip | 0.0015 / 0.0027 | 0.0030 / 0.0042 | 0.0044 / 0.0056 | 0.0060 / 0.0072 | 0.0076 / 0.0087 | LRA | 609.2 / 826.0
RPM | 1198.1 / 1196.7 | 1196.4 / 1195.0 | 1194.7 / 1193.3 | 1192.8 / 1191.4 | 1190.9 / 1189.5 | % | 491.8 / 666.8
L (Inv., MH) | 8.9408 | 8.9408 | 8.9408 | 8.9408 | 8.9408 | LRT (kg.m) | 355.5 / 758.6 |  | 0.13831
(No Load) | 8.9408 |  | Correlated to: Testdata_H402130_Lab#1559A_OD fan610.dat |  |  | % | 58.4 / 124.5
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1723.8149 | 0.028401 | 0.64358
IM/IW | 0.23481 | I*R1/E | 0.0070696 | Rosenberg | 724.5348 | % | 229.7 / 274.9
IW*X/E | 0.21106 | I*R2/E | 0.0059971 | Schwisky | 1259.7211 | Amps | 375.6143
SUM | 0.44587 | Friction/OP. | 0.020107 | Tsurumi | 1001.4122 | Max. Output | 1675.5719 | 0.027583 | 0.65347
IH/I | 0.0111 | Total | 0.044274 | Thrust (1mm) | 8.2253 | % | 224.6075
|  | Efficiency | 0.95573 | Thrust (3 mm) | 17.806 | Amps | 370.085
Single Cage Data | [5 empty] | Miscellaneous Data
Slot Number | 58 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.037032 | Coil Cur. Density
Depth | 38.55 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 252541.5986 | 2.36 / 2.41
Opening | 3.5 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 252.3056 | Bar Cur. Den.
Tip Depth | 3.5 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 539539 | UB: 2.65 / 2.70 | LB: -
Up. Sl. Wid. | 12.05 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.87494 | UER: 2.29 / 2.34 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.21083 | 0.68737 | 124.2328 | 636.3541
0.002 | 177.6014 | 179.856 | 0.79158 | 124.0985 | 641.921
0.01 | 274 | 485.1044 | 0.89579 | 124.0305 | 646.5206
0.062105 | 167.5637 | 548.8335 | 1 | 124 | 650.3937
0.11421 | 141.288 | 568.0291
0.16632 | 131.7949 | 579.2631 | Acceleration Data (FV V)
0.27053 | 127.0231 | 596.0801 | Load Type: | Fan / Pump
0.37474 | 125.5721 | 609.6276 | Load Inertia: | 1586.0 kg.m²
0.47895 | 124.8791 | 620.6453 | Accel. Time: | 9.6 (s)
0.58316 | 124.4713 | 629.3674 | Rated Torque: | 609.2 kg.m
Load
100
99.6
98
83.8526
70.3053
57.4105
38.0105
24.7789
15.6842
9.0105
6.2526
7.8316
14.7053
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | CS6M20U | [5 empty] | HRW / Model Number: | M206FTQL11E-C
Type: TIKE - Form: FCW4 - 6 Pole - 1000 HP - 2300 / 4000 V - 60 Hz - 6811US - Class F | [12 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  |  |  | EPACT | M22 - 26Ga.
Material |  | M36 - 26Ga. |  | NL & Impedance Test | [5 empty] | CS6M20U | CS6900U |  | EQP-III | M36 - 26Ga.
Air Gap |  | 2.1 |  | No load amps |  |  |  | 55 / 32 | 32.7 | #VALUE! | 28 | 28.1 | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 910 |  | No load watts |  |  |  | 10005 | 12675 | 12556.8926 | 8100 | 10166 | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 8,9,9,8 |  | Impedance amps |  | 3 | f | 220 / 175 | 172.5 | #VALUE! | 150 | 146 | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.102"x.204")x2 |  | Impedance volts |  | 3 | f | 460 / 1150 | 1150 | #VALUE! | 1150 | 1150 | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 24138 | 42294 | 39004.0356 | 23128 | 37372 | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 2 x Delta / 2 x Wye |  |  | Winding |  | 80/115 | 76 / 101 | -
MCL |  | 1457 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 11.7264 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.4368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 17 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 220 / 127 |  | #VALUE!
Coil grouping |  | - |  |  |  | RPM |  | 1191
Coil pitch (slot number) |  | 1 ~ 11 |  |  |  | CODE |  | G
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.0995 |  |  |  | DESIGN |  | - |  |  |  |  | Skip
Coil Weight | Wire1 | 938 |  |  |  | Nom.Eff. (%): | [6 empty] | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): | [6 empty] | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%):
FL / LR |  | 241 / 1567 | 270 / 234
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 1431 / 826 | - | #VALUE!
[6 empty] | LRT (%) | 60 | 124 | -
[6 empty] | BDT (%) | 175 | 274 | -
[6 empty] | SLIP (%) |  | 0.72 | -
[5 empty] | IEEE-B | Eff. (%) |  | 96.3 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 88.3 | -
|  |  |  | Losses (Watts) |  | Primary |  | 5926 | -
[6 empty] | Secondary |  | 5163 | -
[6 empty] | Core |  | 4603 | -
[6 empty] | F & W |  | 5092 | -
[6 empty] | Stray |  | 7633 | -
End Ring (Reference) |  |  |  | Note | Outer Fan OD: 610 mm
QCLimits: CS6M20U
|  |  |  | LINK: | H402130.rat @ 1000HP with
Testdata_H402130_Lab#1559A_OD fan610.dat
Run CS6M20U.rat
RSO2: 400-FA31-05P
Approved | S.Hernandez | Design | A. Gracia
Date | 2014-10-02 | Date | 2014-09-17
38.55
3.50
3.50
12.05
62.0
2.83
14.2
051-FA31-01
426.8
35.0
50.5
30.0
50.0
411-FA31
311-FA31
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## Form
Winding Data Calculation
MCL: 1457.0
Coil Resistance |  |  | Lead Resistance
8T: | 0.0159 ~ 0.0153 |  | AWG. 02 x 3
9T: | 0.0179 ~ 0.0172 |  | 0.00151
Coil Dimensions
HM: | 8T: 22.33 | WM: | 8T: 10.76 | WT:
| 9T: 25.12 |  | 9T: 10.76 | 14.30 ~ 13.90
Insulation Allowance |  |  | Wire Weight
Depth: | 11.73 |  | (.102"x.204")x 2: |  | 938 lbs.
Width: | 3.44
QC Resistance
1-2, 2-3, 3-1: |  | 0.208 ~ 0.196

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | L&B ELECTRIC
| TIC SR No.: | 2400576.1
MOTOR NAMEPLATE DATA
| H.P.: | 1000 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1200
| FRAME: | 6811US |  | ENCL: | TEFC |  | FLAMPS: | 127 |  |  | FLRPM: | 1191
| FORM: | FCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40 |  | CODE: | G |  |  | DUTY: | Cont.
| MODEL No.: | GP-10185637 |  |  |  |  | kW:
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 826 |  |  | FULL LOAD (lb-ft.): | 4410 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 120 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 270
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 96.3 | [5 empty] | FULL LOAD: | 88.3
|  | 3/4 LOAD: | 95.6 | [5 empty] | 3/4 LOAD: | 87.5
|  | 1/2 LOAD: | 93.9 | [5 empty] | 1/2 LOAD: | 83.9
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Jerry R
[9 empty] | DATE: | 2026-05-05
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | GP-10185637 |  |  | FLAmps: | 127 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 6811US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1000 | Rotor Inertia: | 1496.8 lb-ft² | Date: | 2026-05-05
FLRPM: | 1191 | Load Inertia: | N/A | File: | CS6M20U
| Locked Rotor Amps: | 826 A | Load Type: | N/A
| Locked Rotor Torque: | 120% | Starting at: | N/A
| Breakdown Torque: | 270% | Accel. Time: | N/A
| Rated Torque: | 4410 lb-ft
Comments: | PROJECT | 2400576.1 |  | D.E.Curve #: | CS6M20U
|  | Prepared by: | Jerry R | Checked by: | SH
Load
100 | 0 | 0.36347 | 100
99 | 175.0329 | 179.8784 | 98
95 | 270 | 485.1327 | 87
90 | 235.3623 | 548.853 | 74
85 | 221.9253 | 568.0452 | 61
80 | 221.2442 | 579.2772 | 50
70 | 220.4274 | 596.0909 | 33
60 | 220 | 609.6356 | 22
50 | 220.5592 | 620.6505 | 14
40 | 221.1163 | 629.3708 | 8
30 | 221.5388 | 636.3561 | 6
20 | 222.0652 | 641.9222 | 8
10 | 222.7549 | 646.5212 | 15
0 | 220 | 650.3937 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | GP-10185637 |  |  | FLAmps: | 127 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 6811US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1000 | Rotor Inertia: | 1496.8 lb-ft² | Date: | 2026-05-05
FLRPM: | 1191 | Load Inertia: | N/A | File: | CS6M20U
Comments: | PROJECT | 2400576.1 |  | D.E.Curve #: | CS6M20U
|  | Prepared by: | Jerry R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
650.3937 | 35 | 15 |  | 650.3937 | 0.0001
573.6035 | 44.9984 | 19.285 |  | 648.4252 | 0.99
496.7902 | 59.9894 | 25.7097 |  | 644.252 | 1.882
420 | 83.9309 | 35.9704 |  | 639.1339 | 2.741
320 | 144.5842 |  |  | 632.8346 | 3.603
220 | 305.8971 |  |  | 625.0394 | 4.499
274 | 197.2057 | 84.5167 |  | 615.1181 | 5.457
180 | 587.4958 | 195.8389 |  | 602.8346 | 6.517
120 | 1028.1541 | 440.6375 |  | 587.6378 | 7.749
110 |  | 900 |  | 573.622 | 8.441
110 |  | 1800 |  | 558.4252 | 9.092
110 |  | 10000 |  | 517.0079 | 9.479
|  |  |  | 332.4409 | 9.54
|  |  |  | 0 | 9.59

## Performance 4000V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | GP-10185637 |  |  | FLAmps: | 127 A
Enclosure: | TEFC | Voltage: | 4000 V | Frame: | 6811US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1000 | Rotor Inertia: | 1496.8 lb-ft² | Date: | 2026-05-05
FLRPM: | 1191 | Load Inertia: | N/A | File: | CS6M20U
| Locked Rotor Amps: | 826 A | Load Type: | N/A
| Locked Rotor Torque: | 124% | Starting at: | N/A
| Breakdown Torque: | 274% | Accel. Time: | N/A
| Rated Torque: | 4410 lb-ft
Comments: | PROJECT | 2400576.1 |  | D.E.Curve #: | CS6M20U
|  | Prepared by: | Jerry R | Checked by: | SH
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 27.4527 | 100 | 0.42589
25 | 88.6976 | 69.7675 | 43.6381 | 81.7361 | 10.5462
50 | 93.9441 | 83.9277 | 68.4993 | 73.1242 | 19.9145
75 | 95.6315 | 87.5014 | 96.8135 | 64.3842 | 29.3447
100 | 96.3389 | 88.2796 | 127.0074 | 55.0711 | 38.8389
125 | 96.6214 | 87.8364 | 159.0938 | 45.6662 | 48.4067
1200
1198
1196
1194
1192
1190
1188
1186
1184
1182
1180
RPM
2000
1000
800
600
400
200
Input Watts (kW)
1200
1400
1600
1800
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance 2300V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | GP-10185637 |  |  | FLAmps: | 220 A
Enclosure: | TEFC | Voltage: | 2300 V | Frame: | 6811US
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1000 | Rotor Inertia: | 1496.8 lb-ft² | Date: | 2026-05-05
FLRPM: | 1191 | Load Inertia: | N/A | File: | CS6M20U
| Locked Rotor Amps: | 1430 A | Load Type: | N/A
| Locked Rotor Torque: | 120% | Starting at: | N/A
| Breakdown Torque: | 270% | Accel. Time: | N/A
| Rated Torque: | 4410 lb-ft
Comments: | PROJECT | 2400576.1 |  | D.E.Curve #: | CS6M20U
|  | Prepared by: | Jerry R | Checked by: | SH
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 47.5495 | 100 | 0.42589
25 | 88.6976 | 69.7675 | 75.5834 | 81.7361 | 10.5462
50 | 93.9441 | 83.9277 | 118.6442 | 73.1242 | 19.9145
75 | 95.6315 | 87.5014 | 167.6859 | 64.3842 | 29.3447
100 | 96.3389 | 88.2796 | 219.9833 | 55.0711 | 38.8389
125 | 96.6214 | 87.8364 | 275.5585 | 45.6662 | 48.4067
1200
1198
1196
1194
1192
1190
1188
1186
1184
1182
1180
RPM
2000
1000
800
600
400
200
Input Watts (kW)
1200
1400
1600
1800
EFF.
P.F.
RPM
AMPS
WATTS
0

## StallTime
Rating: | 6 Pole - 1000.0 HP - 1200 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 9409.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~125 | 124.0 | 22.4 | 0.990 | 823.5 | 266.7 | 851.6
125~250 | 124.1 | 11.3 | 0.892 | 818.2 | 237.6 | 687.9
250~375 | 124.2 | 7.0 | 0.859 | 811.7 | 225.6 | 585.9
375~500 | 124.4 | 7.6 | 0.862 | 803.7 | 222.5 | 511.1
500~625 | 124.7 | 12.3 | 0.896 | 793.8 | 226.1 | 451.4
625~750 | 125.2 | 20.2 | 0.958 | 781.2 | 235.2 | 397.9
750~875 | 126.3 | 31.4 | 1.060 | 765.6 | 251.1 | 346.3
875~1000 | 129.4 | 47.7 | 1.232 | 746.3 | 278.8 | 293.8
1000~1063 | 136.5 | 63.9 | 0.692 | 728.5 | 148.0 | 210.6
1063~1125 | 154.4 | 77.1 | 0.651 | 709.2 | 133.8 | 145.8
1125~1188 | 220.8 | 90.9 | 0.387 | 656.6 | 74.3 | 56.0
1188~1198 | 225.8 | 98.8 | 0.061 | 422.2 | 9.1 | 15.1
1198~1200 | 138.8 | 99.8 | 0.050 | 131.2 | 0.3 | 19.1
Acceleration Time: 9.6 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2309 kW / s |  | 14°C |  | 29°C
Rotor Bar Rise | 4024 kW / s |  | 45°C |  | 90°C
End Ring Rise | 548 kW / s |  | 35°C |  | 70°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 2.0°C / s |  | 322.4 kW | 160°C | 79.5 s
Rotor Bar | 9.1°C / s |  | 814.2 kW | 260°C | 28.5 s
Rotor ER | 7.1°C / s |  | 110.9 kW | 180°C | 25.4 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 76°C + |  | 84°C + | 40°C | = 200°C | 41.7 s
Rotor Bar | 103°C + |  | 157°C + | 40°C | = 300°C | 17.2 s
Rotor ER | 103°C + |  | 77°C + | 40°C | = 220°C | 10.9 s
Cold Stall Time: | 62.8 s |  | Hot Stall Time: |  | 26.8 s