## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RAT FILES\1T2700K_REV1.rat |  |  |  |  | Date: | 2022-04-19 | Time: | 8:34
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 700 | 3600 | DCKW | 4000 | 60 | 105 | 3567.1 / 3559.9 | 0.0091 / 0.0111 | 5012
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 25.4319 | LR Test Data
Air Gap | 2.9 | [5 empty] | Rt. Slot Pitch | 30.88 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 14 | Cross Section Area |  | Mean Value | 28.156 | 539.5489
Core Length | 452 | 452 |  |  | UB: 417.4 | UER: 2800.0 | Eff.T.W.St. | 18.2475 | WS
OD | 590 | 334.2 | Coil Pitch | 0.61899 |  | ERT: 70.0 | Eff.T.W.Rt. | 30.88 | 26267.1494
ID | 340 | 155 | Slot Fill | - |  | ERD1: 246.2 | St.Carter Fac. | 1.3937 | IS
Core Depth | 68 | 54.6 | Con./Slot | 18 |  | ERD2: 332.2 | Rt.Carter Fac. | 1 | 87.4533
Eff.Core L. | 353.4 | 360.84 | Wire Size 1 | (.081"x.204")x1 |  |  | Carter Factor | 1.3937 | Volts / Turn
Slot Data |  |  | Wire Size 2 | (.081"x.182")x1 |  |  | Short. Factor | 0.82618 | 18.3291
Number | 42 | 34 | // Circuits | 1 |  |  | Distrib. Factor | 0.95565 | AC
Kind | Open | Dbl - Closed | Connection | Wye |  |  | Wind. Factor | 0.78954 | 618.9703
Skew | - | 0 | MCL | 1042 | 522 |  | Reactance | (Coeff.: 0.0702)
Depth | 57 | 35 | No.Cond./Ph. | 252 |  |  |  | Running | Start
Width | 14.00 - 14.00 |  | Res. (20°C) | 0.23393 |  |  | Stator Slot | 11.786 | 11.786
Opening | 14 | 0 | (105°C) | 0.31206 | 0.19034 | 0.078464 | Rotor Slot | 29.3457 | 14.9215
Tip Depth | 2.83 | 1 | Material | CU | AL | AL | Zigzag | 7.083 | 6.313
T.Min.Wid. | 11.4319 | 11 | Spec.Resist. | 1.742 | 3.25 | 3.25 | Coil End | 20.3251 | Skew R.: 0.00
Low. R. | 0 | 2 | Spec.Gravity | 8.89 | 2.67 | 2.67 | Belt Leakage | 5.8607 | 5.2704
Up. R. | - | 2 | Weight (kg) |  |  |  | Total Resist. | 0.58087 | 1.1448
Wedge Dep. | 1.20 - 2.40 | Normal | Wire 1 | 72.4934 | 17.1274 | 14.0074 | Total React. | 5.2206 | 4.1097
Duct | 9 x 8 | 8 x 8 | Wire 2 | 64.4421 | - | - | Impedance | 5.2528 | 4.2662
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 33.9879 |  | Length | Section | Density | AT | Volume | Loss |  | 3551.4 | 125RPM |  | Kline/in2
| Reac.= | 33.9965 | Primary Core | 46.3385 | 480.624 | 18.1313 | 929.5391 | 39409.004 | 3666.1741 |  | 3559.9 | 100RPM |  | 116.9757
Excitation Data |  |  | Tooth | 5.7 | 848.4084 | 10.2714 | 14.8277 | 9671.8561 | 358.354 |  | 3568.3 | 75RPM |  | 66.2668
Excit.Amps | 23.786 / 20.977 |  | Second.Core | 20.7502 | 580.4713 | 15.0125 | 188.6604 | Total | 4024.528 |  | 3576.5 | 50RPM |  | 96.8546
Core Loss | 1.106 / 0.975 | Flux / Pole | Tooth | 3.5 | 674.7708 | 12.9145 | 17.6172 | C.L.C. | 1.50 / 0.99 |  | 3584.5 | 25RPM |  | 83.3191
NoLoad | 23.81 / 21.00 | 8.7143 | Air Gap | 0.29 | 1471.4751 | 5.9222 | 1366.6876 | S.F.C. | 6.05 |  |  |  |  | 38.2075
Load Characteristics |  |  | Temp. Rise @ 100%: | 51 / 48 |  | No Load Loss | 11067.2 / 8766.7 | W.Loss | 6036.8 / 3993.9
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 7160.1 / 7568.9 | S.Loss | 1633.4 / 1080.7
Current (A) | 33.37 / 35.02 | 48.87 / 51.28 | 67.41 / 70.74 | 87.45 / 91.77 | 108.61 / 113.97 | Second. Loss | 4971.2 / 5855.3 | Total C.Loss | 7670.2 / 5074.6
Efficiency | 0.916 / 0.900 | 0.949 / 0.933 | 0.958 / 0.941 | 0.959 / 0.943 | 0.958 / 0.942 | Frict.& Wind. | 3000.0 / 3271.9 | Stray Loss | 9929.6426 | 0.959 | 0.943 | 0.98332 | Eff.
P.F. | 0.616 / 0.598 | 0.812 / 0.788 | 0.876 / 0.849 | 0.899 / 0.871 | 0.906 / 0.878 | Starting Data |  | Slip | PF | 0.899 | 0.871 | 0.96885 | PF.
Slip | 0.0023 / 0.0043 | 0.0045 / 0.0065 | 0.0068 / 0.0088 | 0.0091 / 0.0111 | 0.0115 / 0.0135 | LRA | 541.3 / 537.3 |  |  | 87.45 | 91.77 | 1.0494 | Current
RPM | 3591.8 / 3584.5 | 3583.7 / 3576.5 | 3575.5 / 3568.3 | 3567.1 / 3559.9 | 3558.6 / 3551.4 | % | 619.0 / 614.4 |  |  | 3567.1 | 3559.9 | 0.99798 | RPM
L (Inv., MH) | 10.6051 | 9.4494 | 8.8356 | 8.4648 | 8.2202 | LRT (kg.m) | 198.5 / 171.9 |  | 0.26836
(No Load) | 15.2087 |  | Correlated to: 1T2700K_REV1.dat |  |  | % | 139.2 / 120.6
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1367.0362 | 0.051398 | 0.61704
IM/IW | 0.30295 | I*R1/E | 0.011729 | Rosenberg | 316.346 | % | 259.4 / 255.8
IW*X/E | 0.17748 | I*R2/E | 0.0091386 | Schwisky | 503.5175 | Amps | 303.3318 |  |  | HP0.95 | 504.4791
SUM | 0.48044 | Friction/OP. | 0.0057449 | Tsurumi | 185.1431 | Max. Output | 1298.6795 | 0.048683 | 0.63539 | HP1.5 | 18520.2598
IH/I | 0.012741 | Total | 0.039354 | Thrust (1mm) | 81.2568 | % | 248.6939 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.96065 | Thrust (3 mm) | 197.1191 | Amps | 295.0056 |  |  | (RPM/1000)1.8 | 10.031
Double Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 34 | Slit Width | 7 | T.M.Wid.Low. | 11 | Watt Rad. | 0.11255 | Coil Cur. Density |  | k | 0.0685
Depth | 35 | Slit Depth | 8 | Cal.T.W.Up. | 0 | DG2L(cm2) | 43335.5803 | 4.47 / 4.69 |  | Hz | 60
Opening | 0 | L.S.Up.Wid. | 17.5118 | Cal.M.T.Wid. | 0 | GD2L(kg.m2) | 19.3605 | Bar Cur. Den. |  | Load Inertia | 503.1518
Tip Depth | 1 | L.S.Low.Wid. | 13.4346 | Cal.M.T.Wid. | 11 | DO2L(cm2) | 132278 | UB: 3.30 / 3.47 | LB: -
Up. Sl. Wid. | 7 | L.S.Depth | 22 | X2S | 0 | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | 2 | T.M.Wid.Up. | 22.956 | X3S | 0 | Coil Pitch Ct. | 0.67848 | UER: 2.67 / 2.80 | LER: -
S-T Curve Data
Slip | Torque (%) | Amps | Slip | Torque (%) | Amps
0 | 0 | 0 | 0.7 | 153.7127 | 578.3626
0.01 | 103.53 | 87.4507 | 0.8 | 155.8515 | 583.5221
0.05 | 323.9108 | 329.4378 | 0.9 | 159.1856 | 588.2205
0.1 | 317.5299 | 455.5088 | 1 | 163.3896 | 592.5045
0.15 | 267.3212 | 503.237
0.2 | 228.5254 | 525.5202
0.3 | 184.5251 | 546.5946
0.4 | 164.6885 | 557.8024
0.5 | 156.1756 | 565.8977
0.6 | 153.4317 | 572.6429

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | 1T2700K_REV1 | [5 empty] | HRW / Model Number: | 7003WTAK11F-A
Type: TIKK - Form: DCKW - 2 Pole - 700 HP - 2300 / 4000 V - 60 Hz - 5012 - Class F | [9 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [5 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 2.9 |  | No load amps |  |  |  | 36 / 21 | - | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 452 |  | No load watts |  |  |  | 8610 | - | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 9 |  | Impedance amps |  | 3 | f | 92 | - | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.081"x.204")x1 |  | Impedance volts |  | 3 | f | 929 | - | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | (.081"x.182")x1 |  | Impedance watts |  | 3 | f | 28135 | - | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 1D / 1Y |  |  | Winding |  | 80/115 | 46 / 61 | -
MCL |  | 1042 [1071 (1.03)] |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 8.9648 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.2368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 18 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 159 / 92
Coil grouping |  | - |  |  |  | RPM |  | 3560
Coil pitch (slot number) |  | 1 ~ 14 |  |  |  | CODE |  | F
Method of coil connection |  | Adjacent |  |  |  | S. F. |  | 1.15 |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.199 [0.2357 (1.03)] |  |  |  | DESIGN |  |  |  | Skip
Coil Weight | Wire1 | 370 |  |  |  | Nom.Eff. (%): |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%):
FL / LR |  | 393 / 2302 | 346 / 279
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 934/ 539 | -
[6 empty] | LRT (%) | 60 | 120 | -
[6 empty] | BDT (%) | 175 | 255 | -
[6 empty] | SLIP (%) |  | 1.11 | -
[5 empty] | IEEE-B | Eff. (%) |  | 94.5 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 87.1 | -
|  |  |  | Losses (Watts) |  | Primary |  | 6316 | -
[6 empty] | Secondary |  | 5821 | -
[6 empty] | Core |  | 5075 | -
[6 empty] | F & W (A/F Brg) |  | 3272 | -
[6 empty] | Stray |  | 9872 | -
End Ring (Reference) |  |  |  | Note
LINK: 1T2700K_REV1.RAT & DAT
CHG WIRE TO .081x.204x1 ; .081x.182x1
WP-I = 135-R111-100
WP-II = 135-R121-100
LIMITS: 1T2700F=2300V ; 1T2700G=4000V
Approved |  | Design | A. Gracia |  | Revision 1: Complete design changed.
Date |  | Date | 2004-06-25 |  | A. Gracia 06/25/04
REV2. CHG WIRE FROM .091"x.204"x2
JROD 04/19/2022
LAB 8274 - 80.3 AVG Dba
LAB 9636 - DT2700K AVG 79 Dba
lab 3813 - MAX VIBRATION 0.0622 (OEH) LOADED SINWAVE
311-R111
411-R111
340-NT&NB
57.0
2.83
14.0
2800.0
332.2
43.0
70.0
246.2
1.00
35.00
2.0
10.0
7.0
17.51
22.00
13.43
Section
mm2
Section
mm2
M
M
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## Form
Winding Data Calculation
MCL: 1042.0
Coil Resistance |  |  | Lead Resistance
9T: | 0.01443 ~ 0.01387 |  | AWG. 02 x 6
0.00125
Coil Dimensions
HM: | 9T: 22.60 | WM: | 9T: 10.76 | WT:
14.10 ~ 13.70
Insulation Allowance |  |  | Wire Weight
Depth: | 8.96 |  | (.091"x.204")x 2: |  | 370 lbs.
Width: | 3.24
QC Resistance
1-4, 2-5, 3-6: |  | 0.205 ~ 0.193

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | -
| TIC SR No.: | -
MOTOR NAMEPLATE DATA
| H.P.: | 700 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5012USS |  | ENCL: | WP-II |  | FLAMPS: | 92 |  |  | FLRPM: | 3560
| FORM: | DCKW |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TKKH |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | 7003WTAK11F-A |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 539 |  |  | FULL LOAD (lb-ft.): | 1033 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 120 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 255
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 94.5 | [5 empty] | FULL LOAD: | 87.1
|  | 3/4 LOAD: | 94.3 | [5 empty] | 3/4 LOAD: | 84.8
|  | 1/2 LOAD: | 93.5 | [5 empty] | 1/2 LOAD: | 78.7
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Jerry R
[9 empty] | DATE: | 2022-04-18
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | 7003WTAK11F-A |  |  | FLAmps: | 92 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 114.9 lb-ft² | Date: | 2022-04-18
FLRPM: | 3560 | Load Inertia: | N/A | File: | 1T2700K_REV1
| Locked Rotor Amps: | 539 A | Load Type: | N/A
| Locked Rotor Torque: | 120% | Starting at: | N/A
| Breakdown Torque: | 255% | Accel. Time: | N/A
| Rated Torque: | 1033 lb-ft
Comments: | PROJECT | 0 |  | D.E.Curve #: | 1T2700K_REV1
|  | Prepared by: | Jerry R | Checked by:
|  |  | Load | Torque 80% | LRA 80%
100 | 0 | 0.25882 | 100 | 0 | 19.0495
99.78 | 80.86 | 86.2879 | 99.56 | 51.7504 | 69.0303
98.9 | 255 | 326.3496 | 97.725 | 163.2 | 261.0797
93.4667 | 164.0367 | 451.3264 | 83.0133 | 104.9835 | 361.0611
88.0333 | 120.3232 | 498.2715 | 68.8867 | 77.0069 | 398.6172
82.6 | 96.2758 | 520.0349 | 55.72 | 61.6165 | 416.0279
71.7333 | 79.4207 | 540.537 | 35.9467 | 50.8293 | 432.4296
60.8667 | 72.806 | 551.4687 | 22.9533 | 46.5958 | 441.175
50 | 70 | 559.4218 | 14 | 44.8 | 447.5374
40 | 72.4664 | 566.0969 | 8 | 46.3785 | 452.8775
30 | 77.1111 | 571.7654 | 6 | 49.3511 | 457.4123
20 | 85.1796 | 576.8971 | 8 | 54.5149 | 461.5177
10 | 98.5366 | 581.584 | 15 | 63.0634 | 465.2672
0 | 120 | 585.8696 | 30 | 76.8 | 468.6956

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | 7003WTAK11F-A |  |  | FLAmps: | 92 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 114.9 lb-ft² | Date: | 2022-04-18
FLRPM: | 3560 | Load Inertia: | N/A | File: | 1T2700K_REV1
Comments: | PROJECT | 0 |  | D.E.Curve #: | 1T2700K_REV1
|  | Prepared by: | Jerry R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
585.8696 | 24.9 | 16.6 |  | 585.8696 | 0.0001
493.9222 | 35.0335 | 23.3557 |  | 466.9565 | 0.878
401.9473 | 52.9009 | 35.2673 |  | 463.3696 | 1.758
310 | 88.936 | 59.2907 |  | 459.4565 | 2.685
210 | 193.804 |  |  | 455.1087 | 3.703
110 | 706.3433 |  |  | 450.2174 | 4.906
255 | 131.438 | 87.6253 |  | 444.3478 | 6.569
180 | 371.1427 | 175.8591 |  | 436.8478 | 8.913
120 | 593.5246 | 395.6831 |  | 424.2391 | 13.263
110 |  | 800 |  | 407.2826 | 16.495
110 |  | 1600 |  | 379.8913 | 18.003
110 |  | 10000 |  | 311.087 | 18.521
|  |  |  | 0 | 18.545

## Performance 4000V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 7003WTAK11F-A |  |  | FLAmps: | 92 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 114.9 lb-ft² | Date: | 2022-04-18
FLRPM: | 3560 | Load Inertia: | N/A | File: | 1T2700K_REV1
| Locked Rotor Amps: | 539 A | Load Type: | N/A
| Locked Rotor Torque: | 120% | Starting at: | N/A
| Breakdown Torque: | 255% | Accel. Time: | N/A
| Rated Torque: | 1033 lb-ft
Comments: | PROJECT | 0 |  | D.E.Curve #: | 1T2700K_REV1
|  | Prepared by: | Jerry R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 24.7524 | 100 | 0.63993
25 | 90.2 | 59.7 | 35 | 79.5549 | 10.372
50 | 93.5 | 78.7 | 51.2 | 71.5459 | 20.0178
75 | 94.3 | 84.8 | 70.6 | 63.3283 | 29.7701
100 | 94.5 | 87.1 | 92 | 54.9355 | 39.6337
125 | 94.4 | 87.8 | 113.6 | 46.4262 | 49.6138
3600
3590
3580
3570
3560
3550
3540
3530
3520
3510
3500
RPM
1400
700
560
420
280
140
Input Watts (kW)
840
980
1120
1260
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance 2300V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 7003WTAK11F-A |  |  | FLAmps: | 159 A
Enclosure: | WP-II | Voltage: | 2300V | Frame: | 5012USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 114.9 lb-ft² | Date: | 2022-04-18
FLRPM: | 3560 | Load Inertia: | N/A | File: | 1T2700K_REV1
| Locked Rotor Amps: | 934 A | Load Type: | N/A
| Locked Rotor Torque: | 120% | Starting at: | N/A
| Breakdown Torque: | 255% | Accel. Time: | N/A
| Rated Torque: | 1033 lb-ft
Comments: | PROJECT | 0 |  | D.E.Curve #: | 1T2700K_REV1
|  | Prepared by: | Jerry R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 42.8724 | 100 | 0.63993
25 | 90.2 | 59.7 | 60.6218 | 79.5549 | 10.372
50 | 93.5 | 78.7 | 88.681 | 71.5459 | 20.0178
75 | 94.3 | 84.8 | 122.2828 | 63.3283 | 29.7701
100 | 94.5 | 87.1 | 159 | 54.9355 | 39.6337
125 | 94.4 | 87.8 | 196.761 | 46.4262 | 49.6138
3600
3590
3580
3570
3560
3550
3540
3530
3520
3510
3500
RPM
1400
700
560
420
280
140
Input Watts (kW)
840
980
1120
1260
EFF.
P.F.
RPM
AMPS
WATTS
0

## StallTime
Rating: | 2 Pole - 700.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 252.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~360 | 69.9 | 22.5 | 0.878 | 429.6 | 128.1 | 395.6
360~720 | 58.8 | 11.5 | 0.880 | 426.3 | 126.5 | 293.0
720~1080 | 51.9 | 7.0 | 0.927 | 422.7 | 131.1 | 237.1
1080~1440 | 47.9 | 7.0 | 1.018 | 418.7 | 141.4 | 206.2
1440~1800 | 45.6 | 11.0 | 1.203 | 414.2 | 163.9 | 196.4
1800~2191 | 45.7 | 18.5 | 1.663 | 408.8 | 221.2 | 201.1
2191~2582 | 48.7 | 29.4 | 2.344 | 401.9 | 303.0 | 230.7
2582~2974 | 56.2 | 45.8 | 4.350 | 390.3 | 540.1 | 337.3
2974~3169 | 69.3 | 62.3 | 3.232 | 374.7 | 371.4 | 373.9
3169~3365 | 91.0 | 75.9 | 1.508 | 349.5 | 159.1 | 150.0
3365~3560 | 134.1 | 90.4 | 0.518 | 286.2 | 44.8 | 38.3
3560~3567 | 131.6 | 98.6 | 0.024 | 151.9 | 0.2 | 11.0
Acceleration Time: 18.5 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2331 kW / s |  | 37°C |  | 74°C
Rotor Bar Rise | 1891 kW / s |  | 123°C |  | 247°C
End Ring Rise | 780 kW / s |  | 62°C |  | 124°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 3.9°C / s |  | 246.3 kW | 160°C | 40.9 s
Rotor Bar | 28.9°C / s |  | 443.7 kW | 260°C | 9.0 s
Rotor ER | 14.6°C / s |  | 182.9 kW | 180°C | 12.3 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 46°C + |  | 114°C + | 40°C | = 200°C | 29.1 s
Rotor Bar | 58°C + |  | 202°C + | 40°C | = 300°C | 7.0 s
Rotor ER | 58°C + |  | 122°C + | 40°C | = 220°C | 8.4 s
Cold Stall Time: | 24.9 s |  | Hot Stall Time: |  | 16.6 s