## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RAT FILES\1T2M30U.rat |  |  |  |  | Date: | 2022-05-23 | Time: | 12:16
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 1500 | 3600 | DCW4 | 4000 | 60 | 105 | 3569.1 / 3569.1 | 0.0086 / 0.0086 | 5811/12UDZ
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.5437 | LR Test Data
Air Gap | 3.3 | [5 empty] | Rt. Slot Pitch | 30.4569 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 16 | Cross Section Area |  | Mean Value | 27.5003 | 682.3712
Core Length | 555 | 555 |  |  | UB: 406.6 | UER: 3370.3 | Eff.T.W.St. | 14.3389 | WS
OD | 670 | 368.4 | Coil Pitch | 0.62494 |  | ERT: 85.0 | Eff.T.W.Rt. | 30.4569 | 61004.9591
ID | 375 | 185 | Slot Fill | - |  | ERD1: 281.0 | St.Carter Fac. | 1.1789 | IS
Core Depth | 85 | 54.7 | Con./Slot | 20 |  | ERD2: 367.0 | Rt.Carter Fac. | 1 | 186.9028
Eff.Core L. | 441.75 | 441.75 | Wire Size 1 | (.081"x.204")x2 |  |  | Carter Factor | 1.1789 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.83141 | 28.8684
Number | 48 | 38 | // Circuits | 2 |  |  | Distrib. Factor | 0.95544 | AC
Kind | Open | Dbl - Closed | Connection | Wye |  |  | Wind. Factor | 0.79436 | 761.5113
Skew | - | 0 | MCL | 1250 | 640 |  | Reactance | (Coeff.: 0.0313)
Depth | 62.5 | 37 | No.Cond./Ph. | 160 |  |  |  | Running | Start
Width | 10.20 - 10.20 |  | Res. (20°C) | 0.084142 |  |  | Stator Slot | 18.5331 | 18.5331
Opening | 14.5 | 0 | (105°C) | 0.11224 | 0.087481 | 0.029677 | Rotor Slot | 41.6002 | 19.9307
Tip Depth | 2.83 | 1.9 | Material | CU | AL | AL | Zigzag | 4.3345 | 3.9825
T.Min.Wid. | 10.0437 | 11 | Spec.Resist. | 1.742 | 3.25 | 3.25 | Coil End | 21.9398 | Skew R.: 0.00
Low. R. | 0 | 2 | Spec.Gravity | 8.89 | 2.67 | 2.67 | Belt Leakage | 7.2923 | 6.7563
Up. R. | - | 2 | Weight (kg) |  |  |  | Total Resist. | 0.2294 | 0.58212
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 220.8617 | 22.8934 | 18.6298 | Total React. | 2.9371 | 2.2282
Duct | 8 x 10 | 8 x 10 | Wire 2 | - | - | - | Impedance | 2.946 | 2.303
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.0858 |  | Length | Section | Density | AT | Volume | Loss |  | 3561.1 | 125RPM |  | Kline/in2
| Reac.= | 35.0959 | Primary Core | 52.6216 | 750.975 | 18.1653 | 1063.5919 | 69008.2248 | 6439.2955 |  | 3569.1 | 100RPM |  | 117.1953
Excitation Data |  |  | Tooth | 6.25 | 1064.8301 | 12.8111 | 30.6411 | 13310.3758 | 705.4188 |  | 3577.1 | 75RPM |  | 82.6524
Excit.Amps | 45.718 / 40.822 |  | Second.Core | 23.1221 | 755.687 | 18.052 | 455.6938 | Total | 7144.7142 |  | 3584.9 | 50RPM |  | 116.4646
Core Loss | 2.011 / 1.796 | Flux / Pole | Tooth | 3.7 | 923.2575 | 14.7756 | 31.4501 | C.L.C. | 1.75 / 0.66 |  | 3592.4 | 25RPM |  | 95.3264
NoLoad | 45.76 / 40.86 | 13.6417 | Air Gap | 0.33 | 2373.3479 | 5.7479 | 1509.4247 | S.F.C. | 6.05 |  |  |  |  | 37.083
Load Characteristics |  |  | Temp. Rise @ 100%: | 65 / 63 |  | No Load Loss | 20477.6 / 12007.1 | W.Loss | 12503.2 / 4694.4
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 11762.9 / 10701.7 | S.Loss | 1446.7 / 543.2
Current (A) | 67.29 / 69.22 | 102.23 / 105.16 | 143.04 / 147.14 | 186.90 / 192.26 | 233.34 / 240.03 | Second. Loss | 10069.1 / 10006.6 | Total C.Loss | 13950.0 / 5237.6
Efficiency | 0.927 / 0.914 | 0.956 / 0.943 | 0.964 / 0.950 | 0.965 / 0.951 | 0.964 / 0.950 | Frict.& Wind. | 6000.0 / 5497.9 | Stray Loss | 25854.4277 | 0.965 | 0.951 | 0.98549 | Eff.
P.F. | 0.647 / 0.638 | 0.826 / 0.815 | 0.879 / 0.867 | 0.895 / 0.883 | 0.898 / 0.885 | Starting Data |  | Slip | PF | 0.895 | 0.883 | 0.98659 | PF.
Slip | 0.0021 / 0.0021 | 0.0042 / 0.0042 | 0.0064 / 0.0063 | 0.0086 / 0.0086 | 0.0108 / 0.0108 | LRA | 1002.8 / 1144.2 |  |  | 186.90 | 192 | 1.0273 | Current
RPM | 3592.3 / 3592.4 | 3584.8 / 3584.9 | 3577.1 / 3577.1 | 3569.1 / 3569.1 | 3561.1 / 3561.1 | % | 536.5 / 612.2 |  |  | 3569.1 | 3570 | 1.0003 | RPM
L (Inv., MH) | 6.4383 | 5.4994 | 5.0402 | 4.7771 | 4.6049 | LRT (kg.m) | 384.3 / 422.7 |  | 0.25277
(No Load) | 10.0855 |  | Correlated to: lab 9510.dat |  |  | % | 125.8 / 138.4
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 2471.6052 | 0.03986 | 0.62814
IM/IW | 0.27011 | I*R1/E | 0.0090637 | Rosenberg | 410.8443 | % | 219.0 / 266.4
IW*X/E | 0.21526 | I*R2/E | 0.0085863 | Schwisky | 773.0778 | Amps | 545.2858 |  |  | HP0.95 | 1040.6069
SUM | 0.48537 | Friction/OP. | 0.0053619 | Tsurumi | 332.5542 | Max. Output | 2375.1223 | 0.038247 | 0.64206 | HP1.5 | 58094.7502
IH/I | 0.010786 | Total | 0.033798 | Thrust (1mm) | 90.557 | % | 212.254 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.9662 | Thrust (3 mm) | 227.7315 | Amps | 533.9194 |  |  | (RPM/1000)1.8 | 10.031
Double Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 38 | Slit Width | 6 | T.M.Wid.Low. | 11 | Watt Rad. | 0.12436 | Coil Cur. Density |  | k | 0.0685
Depth | 37 | Slit Depth | 9.1 | Cal.T.W.Up. | 0 | DG2L(cm2) | 64466.316 | 4.51 / 4.64 |  | Hz | 60
Opening | 0 | L.S.Up.Wid. | 17.0029 | Cal.M.T.Wid. | 0 | GD2L(kg.m2) | 34.9971 | Bar Cur. Den. |  | Load Inertia | 902.0277
Tip Depth | 1.9 | L.S.Low.Wid. | 13.357 | Cal.M.T.Wid. | 11 | DO2L(cm2) | 213227.5 | UB: 4.18 / 4.30 | LB: -
Up. Sl. Wid. | 6 | L.S.Depth | 22 | X2S | 0 | IMC | 1 | ER Cur. Den. |  |  | 300.6637
Up. Sl. Dep. | 2 | T.M.Wid.Up. | 23.4813 | X3S | 0 | Coil Pitch Ct. | 0.68741 | UER: 3.05 / 3.14 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.23835 | 0.7 | 99.6998 | 582.7366
0.008 | 98.2337 | 106.4519 | 0.8 | 105.8034 | 587.6116
0.04 | 265 | 376.5937 | 0.9 | 116.6129 | 591.9924
0.091429 | 191.1002 | 487.2953 | 1 | 135 | 595.8334
0.14286 | 139.7576 | 523.3146
0.19429 | 115.3902 | 539.5119 | Acceleration Data (FV V)
0.29714 | 99.8251 | 555.0204 | Load Type: | Fan / Pump
0.4 | 95 | 564.0482 | Load Inertia: | 50.7 kg.m²
0.5 | 95.1551 | 571.1434 | Accel. Time: | 3.1 (s)
0.6 | 96.5211 | 577.366 | Rated Torque: | 305.4 kg.m
Load
100
98.4
89.75
76.2286
62.8571
51.2571
33.4857
22
14
8
6
8
15
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | 1T2M30U | [5 empty] | HRW / Model Number:
Type: TIKK - Form: DCW4 - 2 Pole - 1500 HP -2300 / 4000 V - 60 Hz - 5811/12UDZ - Class F | [9 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST | EPACT | M22 - 26Ga.
Material |  |  |  | NL & Impedance Test | [5 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 3.3 |  | No load amps |  |  |  | 41 | - | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 555 |  | No load watts |  |  |  | 12007 | - | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 10 |  | Impedance amps |  | 3 | f | 315 | - | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.081"x.204")x2 |  | Impedance volts |  | 3 | f | 1150 | - | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 61005 | - | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [5 empty] | Dry Kiln
Connection |  | 2 x Delta / 2 x Wye |  |  | Winding |  | 80/115 | 65 / 86 | -
MCL |  | 1250 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 14.522 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 20 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 333 / 192
Coil grouping |  | - |  |  |  | RPM |  | 3565
Coil pitch (slot number) |  | 1 ~ 16 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.0841 |  |  |  | DESIGN |  | - |  | Skip
Coil Weight | Wire1 | 485.9 |  |  |  | Nom.Eff. (%): |  | - |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 464 / 2765 | 430 / 314
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 1981 / 1144 | -
[6 empty] | LRT (%) | 60 | 138 | -
[6 empty] | BDT (%) | 175 | 266 | -
[6 empty] | SLIP (%) |  | 0.86 | -
[5 empty] | IEEE-B | Eff. (%) |  | 95.1 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 88.3 | -
|  |  |  | Losses (Watts) |  | Primary |  | 10702 | -
[6 empty] | Secondary |  | 10007 | -
[6 empty] | Core |  | 5238 | -
[6 empty] | F & W |  | 5498 | -
[6 empty] | Stray |  | 25854 | -
End Ring (Reference) |  |  |  | Note | 1T2M30U
|  |  |  | LINK: | H010234.rat & lab 9510.dat -> Run 1T2M30U.rat
FOR 2300v ONLY PLEASE USE 361-N126-6LDY
DUE TO LEAD CABLE AMP LIMITATIONS
Approved |  | Design | JERRY R
Date |  | Date | 2022-05-23 |  | REV2 UPDATE DATA WITH CORRECT WIRE SIZE
JROD 05/23/2022
62.5
2.83
14.5
3370.3
367.0
43.0
85.0
281.0
1.90
37.00
2.0
11.1
6.0
17.00
22.00
13.36
Section
mm2
Section
mm2
M
M
311-
411-
350-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 2 Pole - 1500.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 300.6 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~360 | 125.8 | 22.5 | 0.261 | 1140.3 | 114.9 | 474.1
360~720 | 111.2 | 11.5 | 0.270 | 1132.4 | 117.5 | 381.9
720~1080 | 102.8 | 7.0 | 0.281 | 1123.5 | 120.5 | 320.6
1080~1440 | 98.1 | 7.0 | 0.296 | 1113.7 | 124.6 | 277.9
1440~1800 | 95.8 | 11.0 | 0.318 | 1102.6 | 131.4 | 247.8
1800~2160 | 95.1 | 18.0 | 0.349 | 1089.8 | 141.4 | 223.9
2160~2530 | 97.4 | 27.7 | 0.397 | 1074.3 | 157.0 | 197.8
2530~2901 | 107.6 | 42.4 | 0.425 | 1050.8 | 162.5 | 165.1
2901~3086 | 127.6 | 57.1 | 0.196 | 1020.3 | 71.0 | 115.4
3086~3271 | 165.4 | 69.5 | 0.144 | 970.2 | 49.1 | 75.5
3271~3456 | 228.1 | 83.0 | 0.095 | 829.3 | 28.1 | 43.7
3456~3569 | 182.5 | 94.1 | 0.096 | 463.7 | 1.2 | 9.3
Acceleration Time: 3.1 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 1219 kW / s |  | 14°C |  | 29°C
Rotor Bar Rise | 1891 kW / s |  | 92°C |  | 185°C
End Ring Rise | 642 kW / s |  | 38°C |  | 77°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 6.0°C / s |  | 513.7 kW | 160°C | 26.5 s
Rotor Bar | 55.0°C / s |  | 1128.0 kW | 260°C | 4.7 s
Rotor ER | 22.9°C / s |  | 382.7 kW | 180°C | 7.8 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 68°C + |  | 92°C + | 40°C | = 200°C | 15.2 s
Rotor Bar | 91°C + |  | 169°C + | 40°C | = 300°C | 3.1 s
Rotor ER | 91°C + |  | 89°C + | 40°C | = 220°C | 3.9 s
Cold Stall Time: | 5.0 s |  | Hot Stall Time: |  | 2.5 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | BARR THORP ELECTRICAL
| TIC SR No.: | 2257472.1
MOTOR NAMEPLATE DATA
| H.P.: | 1500 |  | VOLTS: | 2300/4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812UZ |  | ENCL: | WP-II |  | FLAMPS: | 333/192 |  |  | FLRPM: | 3570
| FORM: | DCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKK |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | WT-10126293 |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 1981/1144 |  |  | FULL LOAD (lb-ft.): | 2207 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 135 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 265
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.1 | [5 empty] | FULL LOAD: | 88.3
|  | 3/4 LOAD: | 95 | [5 empty] | 3/4 LOAD: | 86.7
|  | 1/2 LOAD: | 94.2 | [5 empty] | 1/2 LOAD: | 81.5
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2022-05-23
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | WT-10126293 |  |  | FLAmps: | 333/192 A
Enclosure: | WP-II | Voltage: | 2300/4000 V | Frame: | 5812UZ
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1500 | Rotor Inertia: | 207.6 lb-ft² | Date: | 2022-05-23
FLRPM: | 3565 | Load Inertia: | 300.6 lb-ft² | File: | 1T2M30U
| Locked Rotor Amps: | 1981/1144 A | Load Type: | N/A
| Locked Rotor Torque: | 135% | Starting at: | N/A
| Breakdown Torque: | 265% | Accel. Time: | N/A
| Rated Torque: | 2210 lb-ft
Comments: | PROJECT | 2257472.1 |  | D.E.Curve #: | 1T2M30U
|  | Prepared by: | JERRY R | Checked by:
Load
100 | 0 | 0.23835 | 100
99.2 | 98.2337 | 106.4519 | 98.4
96 | 265 | 376.5937 | 89.75
90.8571 | 191.1002 | 487.2953 | 76.2286
85.7143 | 139.7576 | 523.3146 | 62.8571
80.5714 | 115.3902 | 539.5119 | 51.2571
70.2857 | 99.8251 | 555.0204 | 33.4857
60 | 95 | 564.0482 | 22
50 | 95.1551 | 571.1434 | 14
40 | 96.5211 | 577.366 | 8
30 | 99.6998 | 582.7366 | 6
20 | 105.8034 | 587.6116 | 8
10 | 116.6129 | 591.9924 | 15
0 | 135 | 595.8334 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit Curve
Design Values (For Reference Only)
Model #: | WT-10126293 |  |  | FLAmps: | 333/192 A
Enclosure: | WP-II | Voltage: | 2300/4000 V | Frame: | 5812UZ
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1500 | Rotor Inertia: | 207.6 lb-ft² | Date: | 2022-05-23
FLRPM: | 3565 | Load Inertia: | 300.6 lb-ft² | File: | 1T2M30U
Comments: | PROJECT | 2257472.1 |  | D.E.Curve #: | 1T2M30U
|  | Prepared by: | JERRY R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
595.8333 | 7.0959 | 3.5222 |  | 595.8333 | 0.0001
523.2295 | 9.2018 | 4.5675 |  | 593.9062 | 0.261
450.6039 | 12.407 | 6.1584 |  | 589.7917 | 0.531
378 | 17.6308 | 8.7514 |  | 585.1562 | 0.812
278 | 32.5962 |  |  | 580.0521 | 1.108
178 | 79.509 |  |  | 574.2708 | 1.426
265 | 35.8727 | 17.8061 |  | 567.6042 | 1.775
180 | 100.8269 | 38.5936 |  | 559.5312 | 2.172
145 | 119.8175 | 59.4737 |  | 547.2917 | 2.597
125 |  | 200 |  | 531.4062 | 2.793
125 |  | 400 |  | 505.3125 | 2.937
125 |  | 10000 |  | 431.9271 | 3.032
|  |  |  | 0 | 3.128

## Performance 4000V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | WT-10126293 |  |  | FLAmps: | 192 A
Enclosure: | WP-II | Voltage: | 4000V | Frame: | 5812UZ
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1500 | Rotor Inertia: | 207.6 lb-ft² | Date: | 2022-05-23
FLRPM: | 3565 | Load Inertia: | 300.6 lb-ft² | File: | 1T2M30U
| Locked Rotor Amps: | 1144 A | Load Type: | N/A
| Locked Rotor Torque: | 135% | Starting at: | N/A
| Breakdown Torque: | 265% | Accel. Time: | N/A
| Rated Torque: | 2210 lb-ft
Comments: | PROJECT | 2257472.1 |  | D.E.Curve #: | 1T2M30U
|  | Prepared by: | JERRY R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 47.0118 | 100 | 2
25 | 91.3744 | 63.852 | 69.124 | 83.5509 | 7.6445
50 | 94.2432 | 81.4942 | 105.022 | 64.7408 | 14.8237
75 | 94.9596 | 86.7098 | 146.9406 | 45.4093 | 22.0677
100 | 95.0979 | 88.3493 | 192.0053 | 25.4005 | 29.3809
125 | 94.9974 | 88.5512 | 239.713 | 5.4099 | 36.7649
3600
3596
3592
3588
3584
3580
3576
3572
3568
3564
3560
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance 2300V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | WT-10126293 |  |  | FLAmps: | 333 A
Enclosure: | WP-II | Voltage: | 2300 V | Frame: | 5812UZ
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1500 | Rotor Inertia: | 207.6 lb-ft² | Date: | 2022-05-23
FLRPM: | 3565 | Load Inertia: | 300.6 lb-ft² | File: | 1T2M30U
| Locked Rotor Amps: | 1981 A | Load Type: | N/A
| Locked Rotor Torque: | 135% | Starting at: | N/A
| Breakdown Torque: | 265% | Accel. Time: | N/A
| Rated Torque: | 2210 lb-ft
Comments: | PROJECT | 2257472.1 |  | D.E.Curve #: | 1T2M30U
|  | Prepared by: | JERRY R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 81.4268 | 100 | 2
25 | 91.3744 | 63.852 | 119.7262 | 83.5509 | 7.6445
50 | 94.2432 | 81.4942 | 181.9035 | 64.7408 | 14.8237
75 | 94.9596 | 86.7098 | 254.5085 | 45.4093 | 22.0677
100 | 95.0979 | 88.3493 | 332.5629 | 25.4005 | 29.3809
125 | 94.9974 | 88.5512 | 415.195 | 5.4099 | 36.7649
3600
3596
3592
3588
3584
3580
3576
3572
3568
3564
3560
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0