## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RATFILE\1T2M35U.rat |  |  |  |  | Date: | 2012-01-06 | Time: | 7:49
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 1750 | 3600 | DCW4 | 4000 | 60 | 105 | 3569.4 / 3570.0 | 0.0085 / 0.0083 | 5811/12UDZ
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.5437 | LR Test Data
Air Gap | 3.3 | [5 empty] | Rt. Slot Pitch | 30.4569 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 16 | Cross Section Area |  | Mean Value | 27.5003 | 667.7756
Core Length | 600 | 600 |  |  | UB: 406.6 | UER: 3370.3 | Eff.T.W.St. | 14.3389 | WS
OD | 670 | 368.4 | Coil Pitch | 0.62494 |  | ERT: 85.0 | Eff.T.W.Rt. | 30.4569 | 70159.6251
ID | 375 | 185 | Slot Fill | - |  | ERD1: 281.0 | St.Carter Fac. | 1.1789 | IS
Core Depth | 85 | 54.7 | Con./Slot | 18 |  | ERD2: 367.0 | Rt.Carter Fac. | 1 | 218.8529
Eff.Core L. | 465 | 474.3 | Wire Size 1 | (.102"x.204")x2 |  |  | Carter Factor | 1.1789 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.83141 | 32.076
Number | 48 | 38 | // Circuits | 2 |  |  | Distrib. Factor | 0.95544 | AC
Kind | Open | Dbl - Closed | Connection | Wye |  |  | Wind. Factor | 0.79436 | 802.5189
Skew | - | 0 | MCL | 1295 | 685 |  | Reactance | (Coeff.: 0.0267)
Depth | 62.5 | 37 | No.Cond./Ph. | 144 |  |  |  | Running | Start
Width | 10.20 - 10.20 |  | Res. (20°C) | 0.061921 |  |  | Stator Slot | 18.5331 | 18.5331
Opening | 14.5 | 0 | (105°C) | 0.082602 | 0.075842 | 0.024038 | Rotor Slot | 40.8072 | 19.6603
Tip Depth | 2.83 | 1.9 | Material | CU | AL | AL | Zigzag | 4.3345 | 3.9067
T.Min.Wid. | 10.0437 | 11 | Spec.Resist. | 1.742 | 3.25 | 3.25 | Coil End | 20.8428 | Skew R.: 0.00
Low. R. | 0 | 2 | Spec.Gravity | 8.89 | 2.67 | 2.67 | Belt Leakage | 7.2923 | 6.6346
Up. R. | - | 2 | Weight (kg) |  |  |  | Total Resist. | 0.18248 | 0.48827
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 260.9149 | 24.7497 | 18.6298 | Total React. | 2.4537 | 1.8579
Duct | 10 x 10 | 9 x 10 | Wire 2 | - | - | - | Impedance | 2.4605 | 1.921
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.0858 |  | Length | Section | Density | AT | Volume | Loss
| Reac.= | 35.0959 | Primary Core | 52.6216 | 790.5 | 19.1745 | 1317.9308 | 72640.2367 | 7398.678
Excitation Data |  |  | Tooth | 6.25 | 1120.8738 | 13.5229 | 37.097 | 14010.9219 | 810.5182
Excit.Amps | 57.385 / 66.946 |  | Second.Core | 23.1221 | 811.3692 | 18.6813 | 522.7024 | Total | 8209.1962
Core Loss | 2.314 / 2.700 | Flux / Pole | Tooth | 3.7 | 991.287 | 15.2907 | 36.3731 | C.L.C. | 1.75 / 1.59
NoLoad | 57.43 / 67.00 | 15.1574 | Air Gap | 0.33 | 2523.2435 | 6.0071 | 1577.5066 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 78 / 76 |  | No Load Loss | 22663.3 / 22696.2 | W.Loss | 14366.1 / 13042.7
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 11869.0 / 12437.8 | S.Loss | 1685.5 / 1530.3
Current (A) | 81.47 / 83.38 | 121.18 / 124.03 | 168.16 / 172.11 | 218.85 / 224.00 | 272.50 / 278.91 | Second. Loss | 11563.3 / 9773.0 | Total C.Loss | 16051.6 / 14573.0
Efficiency | 0.931 / 0.920 | 0.959 / 0.947 | 0.966 / 0.954 | 0.967 / 0.956 | 0.966 / 0.955 | Frict.& Wind. | 6000.0 / 7275.0 | Stray Loss | 16201.1338
P.F. | 0.621 / 0.614 | 0.811 / 0.802 | 0.870 / 0.860 | 0.890 / 0.880 | 0.894 / 0.884 | Starting Data |  | Slip | PF
Slip | 0.0021 / 0.0020 | 0.0042 / 0.0040 | 0.0063 / 0.0062 | 0.0085 / 0.0083 | 0.0107 / 0.0105 | LRA | 1202.2 / 1550.9
RPM | 3592.4 / 3593.0 | 3584.9 / 3585.5 | 3577.3 / 3577.8 | 3569.4 / 3570.0 | 3561.5 / 3562.0 | % | 549.3 / 708.7
L (Inv., MH) | 5.2906 | 4.5623 | 4.1954 | 3.9849 | 3.845 | LRT (kg.m) | 476.9 / 711.5 |  | 0.25418
(No Load) | 7.962 |  | Correlated to: 1T2M35U 4000V.dat |  |  | % | 133.9 / 199.7
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 2963.311 | 0.040682 | 0.62715
IM/IW | 0.29212 | I*R1/E | 0.0077895 | Rosenberg | 472.36 | % | 225.1 / 239.6
IW*X/E | 0.20872 | I*R2/E | 0.0084959 | Schwisky | 888.8307 | Amps | 654.2378
SUM | 0.50084 | Friction/OP. | 0.0045959 | Tsurumi | 386.171 | Max. Output | 2845.2882 | 0.039009 | 0.6413
IH/I | 0.010627 | Total | 0.031508 | Thrust (1mm) | 120.888 | % | 217.9462
|  | Efficiency | 0.96849 | Thrust (3 mm) | 303.9636 | Amps | 640.3748
Double Cage Data | [5 empty] | Miscellaneous Data
Slot Number | 38 | Slit Width | 6 | T.M.Wid.Low. | 11 | Watt Rad. | 0.12112 | Coil Cur. Density
Depth | 37 | Slit Depth | 9.1 | Cal.T.W.Up. | 0 | DG2L(cm2) | 69216.4656 | 4.17 / 4.27
Opening | 0 | L.S.Up.Wid. | 17.0029 | Cal.M.T.Wid. | 0 | GD2L(kg.m2) | 37.5758 | Bar Cur. Den.
Tip Depth | 1.9 | L.S.Low.Wid. | 13.357 | Cal.M.T.Wid. | 11 | DO2L(cm2) | 224450 | UB: 4.36 / 4.47 | LB: -
Up. Sl. Wid. | 6 | L.S.Depth | 22 | X2S | 0 | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | 2 | T.M.Wid.Up. | 23.4813 | X3S | 0 | Coil Pitch Ct. | 0.68741 | UER: 3.19 / 3.26 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.25639 | 0.7 | 164.3457 | 677.0576
0.01 | 87.0848 | 121.6308 | 0.8 | 170.5983 | 682.7878
0.05 | 240 | 433.3988 | 0.9 | 181.6036 | 687.925
0.1 | 212.3682 | 564.0569 | 1 | 200 | 692.4108
0.15 | 180.7786 | 606.8429
0.2 | 167.0237 | 626.0623 | Acceleration Data (FV V)
0.3 | 160.5423 | 644.4067 | Load Type: | Fan / Pump
0.4 | 160.3764 | 655.053 | Load Inertia: | 169.2 kg.m²
0.5 | 160 | 663.4113 | Accel. Time: | 4.0 (s)
0.6 | 161.1715 | 670.7363 | Rated Torque: | 356.2 kg.m
Load
100
98
87
74
61
50
33
22
14
8
6
8
15
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | 1T2M35U | [5 empty] | HRW / Model Number: | M403WTQL11F-A |  | BASE : M353WTQL11F-A
Type: TIKK - Form: DCW4 - 2 Pole -2000 HP - 4000 V - 60 Hz - 5811/12UDZ - Class F | [11 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN |  |  |  | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [7 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 3.3 |  | No load amps |  |  |  | 67 | - |  |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 600 |  | No load watts |  |  |  | 22696 | - |  |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 9 |  | Impedance amps |  | 3 | f | 377 | - |  |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (061-0023-04) |  | (.102"x.204")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  |  | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 70160 | - |  |  | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 2 x Wye |  |  | Winding |  | 80/115 | 102 | -
MCL |  | 1295 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 9.4356 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 18 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 256
Coil grouping |  | - |  |  |  | RPM |  | 2565
Coil pitch (slot number) |  | 1 ~ 16 (intersperce One Coil) |  |  |  | CODE |  | F
Method of coil connection |  | Adjacent |  |  |  | S. F. |  | 1.0 |  |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.0624 |  |  |  | DESIGN |  | - |  |  |  | Skip
Coil Weight | Wire1 | 589 |  |  |  | Nom.Eff. (%): |  | - |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 427 / 2957 | 447 / 326
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 1551
[6 empty] | LRT (%) | 60 | 179
[6 empty] | BDT (%) | 175 | 218
[6 empty] | SLIP (%) |  | 0.97
[5 empty] | IEEE-B | Eff. (%) |  | 95.3
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 88.1
|  |  |  | Losses (Watts) |  | Primary |  | 16209
[6 empty] | Secondary |  | 13064
[6 empty] | Core |  | 14738
[6 empty] | F & W |  | 7275
[6 empty] | Stray |  | 21657
|  |  |  | Note | Top Hat WPII. Sleeve Bearing | [5 empty] | NOTE: 2000HP IS NOT SUITABLE FOR ASD DUTY
[5 empty] | F&W Losses for A/F: 5000 W | [5 empty] | NOT SUITABLE FOR HAZARDOUS LOCATION
|  |  |  | LINK: | 1T2M35U_REV1 Link to 1T2M35U_REV1 4000V | [5 empty] | SEE TIR-23847
Approved |  | Design | JERRY R
Date |  | Date | 2021-03-31 |  | REV0. FIRST ISSUE
62.5
2.83
14.5
3370.3
367.0
43.0
85.0
281.0
1.90
37.00
2.0
11.1
6.0
17.00
22.00
13.36
Section
mm2
Section
mm2
M
M
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 2 Pole - 2000.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 1096.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~360 | 161.9 | 22.5 | 0.376 | 1477.2 | 195.3 | 953.0
360~720 | 149.0 | 11.5 | 0.381 | 1466.9 | 195.5 | 786.9
720~1080 | 141.5 | 7.0 | 0.389 | 1455.3 | 196.8 | 670.4
1080~1440 | 137.4 | 7.0 | 0.401 | 1442.5 | 199.7 | 582.2
1440~1800 | 135.5 | 11.0 | 0.421 | 1428.0 | 205.3 | 512.3
1800~2160 | 135.1 | 18.0 | 0.447 | 1411.4 | 213.5 | 450.4
2160~2520 | 135.3 | 27.5 | 0.486 | 1391.3 | 226.2 | 392.3
2520~2880 | 138.5 | 41.5 | 0.540 | 1360.7 | 243.4 | 327.2
2880~3060 | 147.8 | 55.5 | 0.284 | 1321.2 | 120.8 | 239.7
3060~3240 | 168.4 | 67.5 | 0.259 | 1255.8 | 104.0 | 179.0
3240~3420 | 196.4 | 80.5 | 0.226 | 1071.7 | 78.4 | 123.2
3420~3565 | 155.0 | 92.5 | 0.336 | 597.6 | 5.1 | 25.8
Acceleration Time: 4.5 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 1984 kW / s |  | 18°C |  | 37°C
Rotor Bar Rise | 3981 kW / s |  | 180°C |  | 359°C
End Ring Rise | 1262 kW / s |  | 76°C |  | 151°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 6.3°C / s |  | 680.4 kW | 160°C | 25.5 s
Rotor Bar | 86.9°C / s |  | 1926.0 kW | 260°C | 3.0 s
Rotor ER | 36.6°C / s |  | 610.4 kW | 180°C | 4.9 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 105°C + |  | 55°C + | 40°C | = 200°C | 8.8 s
Rotor Bar | 149°C + |  | 111°C + | 40°C | = 300°C | 1.3 s
Rotor ER | 149°C + |  | 31°C + | 40°C | = 220°C | 0.8 s
Cold Stall Time: | 15.0 s |  | Hot Stall Time: |  | 7.0 s

## Form
Winding Data Calculation
|  | MCL: 1295.0 |  | 2 Wye Connection
Coil Resistance |  |  | Lead Resistance
9T: | 0.0159 ~ 0.0153 |  | AWG. 3/0 x 3
0.00058
Coil Dimensions
HM: | 9T: 25.12 | WM: | 9T: 10.76 | WT:
14.60 ~ 14.20
Insulation Allowance |  |  | Wire Weight
Depth: | 9.44 |  | (.102"x.204")x 2: |  | 589 lbs.
Width: | 3.74
QC Resistance
1-2, 2-3, 3-1: |  | 0.130 ~ 0.122

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | DYKMAN ELECTRICAL
| TIC SR No.: | 2213503.1
MOTOR NAMEPLATE DATA
| H.P.: | 2000 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5811USS |  | ENCL: | WP-II |  | FLAMPS: | 256 |  |  | FLRPM: | 3565
| FORM: | DCW4 |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKK |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | WT-10035612 |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 1551 |  |  | FULL LOAD (lb-ft.): | 2946 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 175 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 215
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.3 | [5 empty] | FULL LOAD: | 88.1
|  | 3/4 LOAD: | 95.3 | [5 empty] | 3/4 LOAD: | 86.9
|  | 1/2 LOAD: | 94.8 | [5 empty] | 1/2 LOAD: | 82.3
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2021-03-31
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS
Note on L22: Pick bearings from list!

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | WT-10035612 |  |  | FLAmps: | 256
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5811USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2000 | Rotor Inertia: | 222.9 lb-ft² | Date: | 2021-03-31
FLRPM: | 3565 | Load Inertia: | N/A | File: | H0102822
| Locked Rotor Amps: | 1551 A | Load Type: | N/A
| Locked Rotor Torque: | 175% | Starting at: | N/A
| Breakdown Torque: | 215% | Accel. Time: | N/A
| Rated Torque: | 2946 lb-ft
Comments: | PROJECT | 2213503.1 |  | D.E.Curve #: | H0102822
|  | Prepared by: | JERRY R | Checked by:
Load
100 | 0 | 0.22434 | 100
99.2 | 78.0144 | 106.4121 | 98.4
96 | 215 | 379.1882 | 89.75
90.8889 | 183.7614 | 493.5024 | 76.3111
85.7778 | 152.3182 | 530.9362 | 63.0222
80.6667 | 138.2201 | 547.7514 | 51.4667
70.4444 | 130.6857 | 563.8011 | 33.7556
60.2222 | 130.2057 | 573.1159 | 22.2444
50 | 130 | 580.4287 | 14
40 | 131.4928 | 586.8376 | 8
30 | 135.0995 | 592.3685 | 6
20 | 142.0559 | 597.3821 | 8
10 | 154.3162 | 601.8769 | 15
0 | 175 | 605.8016 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | WT-10035612 |  |  | FLAmps: | 256
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5811USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2000 | Rotor Inertia: | 222.9 lb-ft² | Date: | 2021-03-31
FLRPM: | 3565 | Load Inertia: | N/A | File: | H0102822
1551 A
175%
2946 lb-ft
Comments: | PROJECT | 2213503.1 |  | D.E.Curve #: | H0102822
|  | Prepared by: | JERRY R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
605.8016 | 4.5875 | 2 |  | 605.8016 | 0.0001
563.591 | 5.3004 | 2.3108 |  | 603.8375 | 0.368
521.3677 | 6.1936 | 2.7002 |  | 599.6396 | 0.751
479.1571 | 7.333 | 3.1969 |  | 594.8641 | 1.149
380.5651 | 11.6246 |  |  | 589.5879 | 1.564
281.9731 | 21.1748 |  |  | 583.6184 | 2.001
211.9728 | 37.4692 | 16.3354 |  | 576.7632 | 2.479
177.4656 | 61.7645 | 23.3057 |  | 568.4445 | 3.002
118.3104 | 120.2787 | 52.4379 |  | 555.7739 | 3.585
110 |  | 200 |  | 539.3291 | 3.889
110 |  | 400 |  | 512.2163 | 4.161
110 |  | 10000 |  | 436.3466 | 4.391
|  |  |  | 110 | 4.64

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | WT-10035612 |  |  | FLAmps: | 256
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5811USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2000 | Rotor Inertia: | 222.9 lb-ft² | Date: | 2021-03-31
FLRPM: | 3565 | Load Inertia: | N/A | File: | H0102822
| Locked Rotor Amps: | 1551 A | Load Type: | N/A
| Locked Rotor Torque: | 175% | Starting at: | N/A
| Breakdown Torque: | 215% | Accel. Time: | N/A
| Rated Torque: | 2946 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 3600 | 4000
[8 empty] | 3595 | 3600
Comments: | PROJECT | 2213503.1 |  | D.E.Curve #: | H0102822 |  |  | 3590 | 3200
[8 empty] | 3585 | 2800
[8 empty] | 3580 | 2400
[8 empty] | 3575 | 2000
|  | Prepared by: | JERRY R | Checked by: |  | SYNC SPEED | 3600 | 3570 | 1600
[6 empty] | NEW SPEED LOWER RANGE | 3550 | 3565 | 1200
[6 empty] | NEW kW UPPER RANGE | 4000 | 3560 | 800
[8 empty] | 3555 | 400
[8 empty] | 3550 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 69 | 100 | 0.57293
25 | 92.5 | 65.6 | 88.79 | 82.6907 | 10.0885
50 | 94.8 | 82.3 | 137.93 | 65.7783 | 19.6616
75 | 95.3 | 86.9 | 194.93 | 48.481 | 29.3399
100 | 95.3 | 88.1 | 256.25 | 30 | 39.1021
125 | 95.2 | 88 | 321.6 | 12.1094 | 49.0184
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 59.0689 | 100 | 22.9713
25 | 92.4491 | 65.5126 | 88.7893 | 84.1392 | 10.0747
50 | 94.7809 | 82.2711 | 137.9274 | 66.9732 | 19.6538
75 | 95.2832 | 86.8596 | 194.9288 | 49.376 | 29.3252
100 | 95.2938 | 88.0894 | 256.2479 | 30.606 | 39.096
125 | 95.1077 | 87.9069 | 321.6028 | 12.3946 | 48.9656
3600
3595
3590
3585
3580
3575
3570
3565
3560
3555
3550
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0