## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RAT FILES\1T4450K REV1.rat |  |  |  |  | Date: | 2025-05-20 | Time: | 7:10
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
4 | 450 | 1800 | DCKW | 4000 | 60 | 105 | 1776.3 / 1770.6 | 0.0131 / 0.0163 | 5012
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 20.4203 | LR Test Data
Air Gap | 1.7 | [5 empty] | Rt. Slot Pitch | 27.6032 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 14 | Cross Section Area |  | Mean Value | 24.0117 | 558.2877
Core Length | 395 | 395 |  |  | UB: 264.6 | UER: 2000.0 | Eff.T.W.St. | 12.4165 | WS
OD | 590 | 386.6 | Coil Pitch | 0.86658 |  | ERT: 50.0 | Eff.T.W.Rt. | 27.6032 | 20793.0291
ID | 390 | 220 | Slot Fill | - |  | ERD1: 299.0 | St.Carter Fac. | 1.2245 | IS
Core Depth | 54 | 55.5 | Con./Slot | 17 |  | ERD2: 385.0 | Rt.Carter Fac. | 1 | 59.4282
Eff.Core L. | 292.95 | 292.95 | Wire Size 1 | (.064"x.162")x1 |  |  | Carter Factor | 1.2245 | Volts / Turn
Slot Data |  |  | Wire Size 2 | (.064"x.144")x1 |  |  | Short. Factor | 0.97812 | 13.5851
Number | 60 | 44 | // Circuits | 1 |  |  | Distrib. Factor | 0.95651 | AC
Kind | Open | Dbl - Closed | Connection | Wye |  |  | Wind. Factor | 0.93558 | 494.7416
Skew | - | 0 | MCL | 900 | 445 |  | Reactance | (Coeff.: 0.0983)
Depth | 46 | 27.8 | No.Cond./Ph. | 340 |  |  |  | Running | Start
Width | 8.00 - 8.00 |  | Res. (20°C) | 0.44359 |  |  | Stator Slot | 18.6943 | 18.6943
Opening | 11.6 | 0 | (105°C) | 0.59174 | 0.50559 | 0.090698 | Rotor Slot | 31.9341 | 18.1056
Tip Depth | 2.83 | 0.8 | Material | CU | AL | AL | Zigzag | 8.2551 | 5.8281
T.Min.Wid. | 8.8203 | 12 | Spec.Resist. | 1.742 | 3.25 | 3.25 | Coil End | 17.4455 | Skew R.: 0.00
Low. R. | 0 | 2 | Spec.Gravity | 8.89 | 2.67 | 2.67 | Belt Leakage | 5.4616 | 3.8559
Up. R. | - | 2 | Weight (kg) |  |  |  | Total Resist. | 1.188 | 1.9625
Wedge Dep. | 2.83 - 0.50 | Magnetic | Wire 1 | 52.0672 | 12.2785 | 12.0117 | Total React. | 8.0409 | 6.285
Duct | 8 x 10 | 8 x 10 | Wire 2 | 46.0018 | - | - | Impedance | 8.1282 | 6.5842
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 26.9962 |  | Length | Section | Density | AT | Volume | Loss |  | 1764.5 | 125RPM |  | Kline/in2
| Reac.= | 26.9989 | Primary Core | 23.1692 | 316.386 | 17.2279 | 531.2877 | 26637.9976 | 2281.1916 |  | 1770.6 | 100RPM |  | 111.1475
Excitation Data |  |  | Tooth | 4.6 | 387.5876 | 14.0631 | 40.545 | 7131.6111 | 439.5828 |  | 1776.7 | 75RPM |  | 90.7292
Excit.Amps | 21.179 / 18.799 |  | Second.Core | 12.9983 | 325.1745 | 16.7623 | 259.4177 | Total | 2720.7745 |  | 1782.6 | 50RPM |  | 108.1435
Core Loss | 0.735 / 0.652 | Flux / Pole | Tooth | 2.78 | 386.694 | 14.0956 | 24.7045 | C.L.C. | 1.50 / 1.10 |  | 1787.0 | 25RPM |  | 90.9389
NoLoad | 21.19 / 18.81 | 5.4507 | Air Gap | 0.17 | 787.9503 | 6.9175 | 935.8153 | S.F.C. | 6.05 |  |  |  |  | 44.6291
Load Characteristics |  |  | Temp. Rise @ 100%: | 63 / 62 |  | No Load Loss | 7293.2 / 7401.1 | W.Loss | 4081.2 / 2994.0
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 6269.6 / 7096.9 | S.Loss | 1015.1 / 744.7
Current (A) | 23.24 / 23.77 | 35.36 / 36.16 | 46.71 / 47.76 | 59.43 / 60.77 | 73.13 / 74.78 | Second. Loss | 4633.4 / 5622.9 | Total C.Loss | 5096.3 / 3738.7
Efficiency | 0.914 / 0.895 | 0.945 / 0.925 | 0.952 / 0.932 | 0.952 / 0.932 | 0.949 / 0.929 | Frict.& Wind. | 1600.0 / 3440.4 | Stray Loss | 4527.4238 | 0.952 | 0.932 | 0.97899 | Eff.
P.F. | 0.570 / 0.569 | 0.725 / 0.724 | 0.817 / 0.816 | 0.856 / 0.855 | 0.873 / 0.872 | Starting Data |  | Slip | PF | 0.856 | 0.855 | 0.99883 | PF.
Slip | 0.0040 / 0.0072 | 0.0065 / 0.0097 | 0.0098 / 0.0129 | 0.0131 / 0.0163 | 0.0166 / 0.0197 | LRA | 350.8 / 368.1 |  |  | 59.43 | 61 | 1.0264 | Current
RPM | 1792.8 / 1787.0 | 1788.3 / 1782.6 | 1782.4 / 1776.7 | 1776.3 / 1770.6 | 1770.2 / 1764.5 | % | 590.2 / 619.3 |  |  | 1776.3 | 1770 | 0.99645 | RPM
L (Inv., MH) | 16.6939 | 15.1392 | 14.3557 | 13.8544 | 13.494 | LRT (kg.m) | 274.3 / 276.5 |  | 0.29807
(No Load) | 21.0044 |  | Correlated to: 1T4450K.dat |  |  | % | 149.0 / 150.2
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 857.5285 | 0.073957 | 0.58628
IM/IW | 0.41615 | I*R1/E | 0.015103 | Rosenberg | 410.4072 | % | 252.1 / 284.1
IW*X/E | 0.1772 | I*R2/E | 0.01314 | Schwisky | 743.495 | Amps | 195.4969 |  |  | HP0.95 | 331.5522
SUM | 0.59335 | Friction/OP. | 0.0047662 | Tsurumi | 615.835 | Max. Output | 796.6086 | 0.068347 | 0.61268 | HP1.5 | 9545.9421
IH/I | 0.012466 | Total | 0.045476 | Thrust (1mm) | 122.35 | % | 237.2978 |  |  | (RPM/1000)2.4 | 4.0988
|  | Efficiency | 0.95452 | Thrust (3 mm) | 244.4755 | Amps | 187.6636 |  |  | (RPM/1000)1.8 | 2.8807
Double Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 24
Slot Number | 44 | Slit Width | 6 | T.M.Wid.Low. | 12 | Watt Rad. | 0.098451 | Coil Cur. Density |  | k | 0.0685
Depth | 27.8 | Slit Depth | 7 | Cal.T.W.Up. | 0 | DG2L(cm2) | 47079.7614 | 4.95 / 5.06 |  | Hz | 60
Opening | 0 | L.S.Up.Wid. | 13.9316 | Cal.M.T.Wid. | 0 | GD2L(kg.m2) | 26.7388 | Bar Cur. Den. |  | Load Inertia | 1714.3773
Tip Depth | 0.8 | L.S.Low.Wid. | 11.6429 | Cal.M.T.Wid. | 12 | DO2L(cm2) | 109651.5 | UB: 4.17 / 4.27 | LB: -
Up. Sl. Wid. | 6 | L.S.Depth | 16 | X2S | 0 | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | 2 | T.M.Wid.Up. | 20.9177 | X3S | 0 | Coil Pitch Ct. | 0.89993 | UER: 1.94 / 1.98 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.34741 | 0.7 | 110.3203 | 591.2001
0.004 | 60.5907 | 70.5544 | 0.8 | 117.1971 | 595.6776
0.02 | 229.8826 | 266.9849 | 0.9 | 129.4043 | 599.6582
0.04 | 280 | 411.8415 | 1 | 150 | 603.2787
0.1 | 185.5979 | 482.4672
0.16 | 148.1377 | 519.2895 | Acceleration Data (FV V)
0.28 | 117.6624 | 553.9834 | Load Type: | Fan / Pump
0.4 | 105 | 569.9099 | Load Inertia: | 144.5 kg.m²
0.5 | 105.2722 | 579.3176 | Accel. Time: | 4.4 (s)
0.6 | 106.7749 | 585.9467 | Rated Torque: | 184.1 kg.m
Load
100
99.2
95.25
89.75
74
58.8
36.4
22
14
8
6
8
15
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | 1T4450K REV1 | [5 empty] | HRW / Model Number: | 4504WTAK11F-A
Type: TIKK - Form: DCKW - 4 Pole - 450 HP - 2300 / 4000 V - 60 Hz - 5012 - Class F | [9 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST | EPACT | M22 - 26Ga.
Material |  | NCB1 - 26Ga. |  | NL & Impedance Test | [5 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 1.7 |  | No load amps |  |  |  | 33 / 18.8 | - | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 395 |  | No load watts |  |  |  | 7401 | - | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 8,9 |  | Impedance amps |  | 3 | f | 122 | - | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.064"x.162")x1 |  | Impedance volts |  | 3 | f | 1150 | - | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | (.064"x.144")x1 |  | Impedance watts |  | 3 | f | 20793 | - | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [5 empty] | Dry Kiln
Connection |  | 1D / 1Y |  |  | Winding |  | 80/115 | 63 / 83 | -
MCL |  | 900 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 12.1348 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.4276 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 17 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 106 / 61
Coil grouping |  | - |  |  |  | RPM |  | 1770
Coil pitch (slot number) |  | 1 ~ 14 |  |  |  | CODE |  | G
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.4436 |  |  |  | DESIGN |  | - |  | Skip
Coil Weight | Wire1 | 114.5 |  |  |  | Nom.Eff. (%): |  | - |  | Adjacent
(lbs.) | Wire2 | 101.2 |  |  |  | Min.Eff. (%): |  | - |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 506 / 3053 | 427 / 198
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | 708 / 409 | 637/ 368 | -
[6 empty] | LRT (%) | 80 | 150 | -
[6 empty] | BDT (%) | 175 | 284 | -
[6 empty] | SLIP (%) |  | 1.63 | -
[5 empty] | IEEE-B | Eff. (%) |  | 93.2 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 85.5 | -
|  |  |  | Losses (Watts) |  | Primary |  | 7097 | -
[6 empty] | Secondary |  | 5623 | -
[6 empty] | Core |  | 3739 | -
[6 empty] | F & W |  | 3440 | -
[6 empty] | Stray |  | 4527 | -
End Ring (Reference) |  |  |  | Note
LINK: 1T4450K.RAT AND DAT
THEN RUN 1T4450K REV1
Approved |  | Design | Jerry R
Date |  | Date | 2025-05-20 |  | REV1. CHG FROM EDS-C-1059-3
CHG FROM 0.064"x.162"x2 JROD 05/20/2025
46.0
2.83
11.6
2000.0
385.0
43.0
50.0
299.0
0.80
27.80
2.0
9.0
6.0
13.93
16.00
11.64
Section
mm2
Section
mm2
M
M
311-
411-
350-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
CUSTOMER:
TIC SR No.:
MOTOR NAMEPLATE DATA
| H.P.: | 450 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1800
| FRAME: | 5012US |  | ENCL: | WP-II |  | FLAMPS: | 61 |  |  | FLRPM: | 1770
| FORM: | DCKW |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKK |  | AMB.: | 40 |  | CODE: | G |  |  | DUTY: | Cont.
| MODEL No.: | [5 empty] | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 368 |  |  | FULL LOAD (lb-ft.): | 1335 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 150 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 280
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 93.2 | [5 empty] | FULL LOAD: | 85.5
|  | 3/4 LOAD: | 93.2 | [5 empty] | 3/4 LOAD: | 81.6
|  | 1/2 LOAD: | 92.5 | [5 empty] | 1/2 LOAD: | 72.4
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Jerry R
[9 empty] | DATE: | 2025-05-20
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | 0 |  |  | FLAmps: | 61 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 450 | Rotor Inertia: | 158.6 lb-ft² | Date: | 2025-05-20
FLRPM: | 1770 | Load Inertia: | N/A | File: | 1T4450K REV1
| Locked Rotor Amps: | 368 A | Load Type: | N/A
| Locked Rotor Torque: | 150% | Starting at: | N/A
| Breakdown Torque: | 280% | Accel. Time: | N/A
| Rated Torque: | 1335 lb-ft
Comments: | PROJECT | 0 |  | D.E.Curve #: | 1T4450K REV1
ASSUMED 1/2 NEMA
|  | Prepared by: | Jerry R | Checked by:
100 | 0 | 0.34741
99.6 | 60.5907 | 70.5544
98 | 229.8826 | 266.9849
96 | 280 | 411.8415
90 | 185.5979 | 482.4672
84 | 148.1377 | 519.2895
72 | 117.6624 | 553.9834
60 | 105 | 569.9099
50 | 105.2722 | 579.3176
40 | 106.7749 | 585.9467
30 | 110.3203 | 591.2001
20 | 117.1971 | 595.6776
10 | 129.4043 | 599.6582
0 | 150 | 603.2787

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | 0 |  |  | FLAmps: | 61 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 450 | Rotor Inertia: | 158.6 lb-ft² | Date: | 2025-05-20
FLRPM: | 1770 | Load Inertia: | N/A | File: | 1T4450K REV1
Comments: | PROJECT | 0 |  | D.E.Curve #: | 1T4450K REV1
ASSUMED 1/2 NEMA
|  | Prepared by: | Jerry R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
603.2787 | 14.3683 | 7.7404 |  | 603.2787 | 0.0001
600 | 14.5258 | 7.8252 |  | 601.4754 | 0.381
500 | 20.9171 | 11.2684 |  | 597.7049 | 0.78
400 | 32.683 | 17.6068 |  | 593.4426 | 1.198
300 | 58.103 |  |  | 588.5246 | 1.638
200 | 130.7318 |  |  | 582.623 | 2.108
280 | 66.6999 | 35.9323 |  | 574.5902 | 2.621
180 | 163.1661 | 86.9472 |  | 561.9672 | 3.274
145 | 248.7169 | 133.9876 |  | 536.5574 | 3.902
125 |  | 300 |  | 500.8197 | 4.169
125 |  | 600 |  | 447.2131 | 4.347
125 |  | 10000 |  | 339.3443 | 4.402
|  |  |  | 0 | 4.447

## Performance 4000V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 0 |  |  | FLAmps: | 61 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 450 | Rotor Inertia: | 158.6 lb-ft² | Date: | 2025-05-20
FLRPM: | 1770 | Load Inertia: | N/A | File: | 1T4450K REV1
| Locked Rotor Amps: | 368 A | Load Type: | N/A
| Locked Rotor Torque: | 150% | Starting at: | N/A
| Breakdown Torque: | 280% | Accel. Time: | N/A
| Rated Torque: | 1335 lb-ft
Comments: | PROJECT | 0 |  | D.E.Curve #: | 1T4450K REV1
ASSUMED 1/2 NEMA
|  | Prepared by: | Jerry R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 21.7515 | 100 | 0.74011
25 | 89.5126 | 56.933 | 23.8552 | 66.2955 | 9.4093
50 | 92.5186 | 72.4166 | 36.2906 | 55.2058 | 18.2071
75 | 93.2053 | 81.6211 | 47.9413 | 40.4486 | 27.1094
100 | 93.2024 | 85.5372 | 60.9971 | 25.3257 | 36.147
125 | 92.9053 | 87.167 | 75.0601 | 9.8963 | 45.3283
1800
1796
1792
1788
1784
1780
1776
1772
1768
1764
1760
RPM
1000
500
400
300
200
100
Input Watts (kW)
600
700
800
900
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance 2300V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 0 |  |  | FLAmps: | 106 A
Enclosure: | WP-II | Voltage: | 2300 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 450 | Rotor Inertia: | 158.6 lb-ft² | Date: | 2025-05-20
FLRPM: | 1770 | Load Inertia: | N/A | File: | 1T4450K REV1
| Locked Rotor Amps: | 637 A | Load Type: | N/A
| Locked Rotor Torque: | 150% | Starting at: | N/A
| Breakdown Torque: | 280% | Accel. Time: | N/A
| Rated Torque: | 1335 lb-ft
Comments: | PROJECT | 0 |  | D.E.Curve #: | 1T4450K REV1
ASSUMED 1/2 NEMA
|  | Prepared by: | Jerry R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 37.6747 | 100 | 0.74011
25 | 89.5126 | 56.933 | 41.3185 | 66.2955 | 9.4093
50 | 92.5186 | 72.4166 | 62.8572 | 55.2058 | 18.2071
75 | 93.2053 | 81.6211 | 83.0368 | 40.4486 | 27.1094
100 | 93.2024 | 85.5372 | 106 | 25.3257 | 36.147
125 | 92.9053 | 87.167 | 130.0079 | 9.8963 | 45.3283
1800
1796
1792
1788
1784
1780
1776
1772
1768
1764
1760
RPM
1000
500
400
300
200
100
Input Watts (kW)
600
700
800
900
EFF.
P.F.
RPM
AMPS
WATTS
0

## StallTime
Rating: | 4 Pole - 450.0 HP - 1800 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 857.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~180 | 139.7 | 22.5 | 0.381 | 366.9 | 91.6 | 190.4
180~360 | 123.3 | 11.5 | 0.399 | 364.6 | 94.9 | 155.0
360~540 | 113.8 | 7.0 | 0.418 | 362.0 | 98.0 | 130.6
540~720 | 108.5 | 7.0 | 0.440 | 359.0 | 101.5 | 113.2
720~900 | 106.0 | 11.0 | 0.470 | 355.4 | 106.6 | 100.3
900~1080 | 105.1 | 18.0 | 0.513 | 350.5 | 113.6 | 89.9
1080~1296 | 111.3 | 29.2 | 0.653 | 342.8 | 140.0 | 76.1
1296~1512 | 132.9 | 47.6 | 0.628 | 327.3 | 127.3 | 57.5
1512~1620 | 166.9 | 66.4 | 0.267 | 305.5 | 47.5 | 35.1
1620~1728 | 232.8 | 81.9 | 0.178 | 272.8 | 27.3 | 18.3
1728~1764 | 254.9 | 92.5 | 0.055 | 207.0 | 6.2 | 10.3
1764~1776 | 164.9 | 97.2 | 0.045 | 102.9 | 0.3 | 6.6
Acceleration Time: 4.4 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 955 kW / s |  | 25°C |  | 51°C
Rotor Bar Rise | 834 kW / s |  | 76°C |  | 152°C
End Ring Rise | 150 kW / s |  | 14°C |  | 28°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 7.3°C / s |  | 275.6 kW | 160°C | 21.9 s
Rotor Bar | 38.8°C / s |  | 427.0 kW | 260°C | 6.7 s
Rotor ER | 7.1°C / s |  | 76.6 kW | 180°C | 25.3 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 63°C + |  | 97°C + | 40°C | = 200°C | 13.3 s
Rotor Bar | 83°C + |  | 177°C + | 40°C | = 300°C | 4.6 s
Rotor ER | 83°C + |  | 97°C + | 40°C | = 220°C | 13.6 s
Cold Stall Time: | 10.1 s |  | Hot Stall Time: |  | 5.4 s