## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\Top_Hat_5812_Expansion\Electric\Series-Design\WPII\6pole\2T6800U.rat |  |  |  |  | Date: | 2022-11-01 | Time: | 10:53
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
6 | 800 | 1200 | DCKW | 4000 | 60 | 105 | 1185.5 / 1180.0 | 0.0121 / 0.0167 | 5811/12
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 26.4708 | LR Test Data
Air Gap | 1.6 | [5 empty] | Rt. Slot Pitch | 33.7945 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 9 | Cross Section Area |  | Mean Value | 30.1327 | 547.1493
Core Length | 620 | 620 |  |  | UB: 356.6 | UER: 1800.0 | Eff.T.W.St. | 16.8163 | WS
OD | 670 | 451.8 | Coil Pitch | 0.8888 |  | ERT: 35.0 | Eff.T.W.Rt. | 33.7945 | 33812.1165
ID | 455 | 270 | Slot Fill | - |  | ERD1: 340.0 | St.Carter Fac. | 1.2392 | IS
Core Depth | 54.5 | 60.2 | Con./Slot | 26 |  | ERD2: 450.0 | Rt.Carter Fac. | 1 | 110.4196
Eff.Core L. | 455.7 | 455.7 | Wire Size 1 | (.051"x.204")x1 |  |  | Carter Factor | 1.2392 | Volts / Turn
Slot Data |  |  | Wire Size 2 | (.051"x.182")x1 |  |  | Short. Factor | 0.98478 | 19.739
Number | 54 | 42 | // Circuits | 2 |  |  | Distrib. Factor | 0.95964 | AC
Kind | Open | Dbl - Closed | Connection | Wye |  |  | Wind. Factor | 0.94503 | 542.2785
Skew | - | 0.8 | MCL | 1010 | 655.539 |  | Reactance | (Coeff.: 0.0820)
Depth | 53 | 30.7 | No.Cond./Ph. | 234 |  |  |  | Running | Start
Width | 9.65 - 9.65 |  | Res. (20°C) | 0.17037 |  |  | Stator Slot | 16.9983 | 16.9983
Opening | 13.8 | 0 | (105°C) | 0.22727 | 0.27979 | 0.028363 | Rotor Slot | 20.6086 | 11.0251
Tip Depth | 2.83 | 0.7 | Material | CU | AL | AL | Zigzag | 11.438 | 5.9109
T.Min.Wid. | 12.6708 | 17.5 | Spec.Resist. | 1.742 | 3.25 | 3.25 | Coil End | 5.2374 | Skew R.: 0.55
Low. R. | 0 | 2 | Spec.Gravity | 8.89 | 2.67 | 2.67 | Belt Leakage | 3.7952 | 2.2209
Up. R. | - | 2 | Weight (kg) |  |  |  | Total Resist. | 0.53543 | 0.9244
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 80.7214 | 24.8149 | 12.6948 | Total React. | 5.3122 | 3.3719
Duct | 13 x 10 | 13 x 10 | Wire 2 | 71.596 | - | - | Impedance | 5.3391 | 3.4963
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 29.9935 |  | Length | Section | Density | AT | Volume | Loss |  | 1176.2 | 125RPM |  | Kline/in2
| Reac.= | 29.9982 | Primary Core | 17.5405 | 496.713 | 15.7848 | 490.1619 | 48023.4223 | 3569.1499 |  | 1180.0 | 100RPM |  | 101.8373
Excitation Data |  |  | Tooth | 5.3 | 519.6677 | 15.0876 | 109.0696 | 16525.4328 | 1141.5103 |  | 1183.7 | 75RPM |  | 97.3389
Excit.Amps | 44.816 / 41.988 |  | Second.Core | 10.2206 | 548.6628 | 14.2902 | 149.1693 | Total | 4710.6602 |  | 1187.3 | 50RPM |  | 92.1949
Core Loss | 1.074 / 1.007 | Flux / Pole | Tooth | 3.07 | 558.2325 | 14.0453 | 41.5283 | C.L.C. | 1.10 / 1.09 |  | 1190.8 | 25RPM |  | 90.6144
NoLoad | 44.83 / 42.00 | 7.8405 | Air Gap | 0.16 | 942.0234 | 8.3231 | 1059.7263 | S.F.C. | 6.05 |  |  |  |  | 53.6971
Load Characteristics |  |  | Temp. Rise @ 100%: | 77 / 76 |  | No Load Loss | 10978.5 / 10857.4 | W.Loss | 5181.7 / 5145.6
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 8313.1 / 9021.3 | S.Loss | 2270.2 / 2254.4
Current (A) | 53.52 / 55.14 | 68.13 / 70.20 | 87.83 / 90.50 | 110.42 / 113.78 | 135.23 / 139.34 | Second. Loss | 7577.6 / 7823.6 | Total C.Loss | 7451.9 / 7400.0
Efficiency | 0.925 / 0.911 | 0.954 / 0.940 | 0.960 / 0.946 | 0.961 / 0.946 | 0.959 / 0.944 | Frict.& Wind. | 2500.0 / 2500.0 | Stray Loss | 7172.4282 | 0.961 | 0.946 | 0.98439 | Eff.
P.F. | 0.435 / 0.429 | 0.663 / 0.653 | 0.766 / 0.755 | 0.812 / 0.800 | 0.831 / 0.819 | Starting Data |  | Slip | PF | 0.812 | 0.800 | 0.98522 | PF.
Slip | 0.0030 / 0.0076 | 0.0059 / 0.0106 | 0.0090 / 0.0136 | 0.0121 / 0.0167 | 0.0153 / 0.0199 | LRA | 660.5 / 729.2 |  |  | 110.42 | 114 | 1.0324 | Current
RPM | 1196.4 / 1190.8 | 1192.9 / 1187.3 | 1189.3 / 1183.7 | 1185.5 / 1180.0 | 1181.7 / 1176.2 | % | 598.2 / 660.4 |  |  | 1185.5 | 1180.0 | 0.99536 | RPM
L (Inv., MH) | 9.8373 | 9.3091 | 8.9475 | 8.608 | 8.3345 | LRT (kg.m) | 742.2 / 733.8 |  | 0.2644
(No Load) | 11.5556 |  | Correlated to: 2N6800U(EST).dat |  |  | % | 151.4 / 149.7
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1298.0911 | 0.057956 | 0.58682
IM/IW | 0.495 | I*R1/E | 0.010812 | Rosenberg | 1078.2321 | % | 214.9 / 219.5
IW*X/E | 0.20825 | I*R2/E | 0.01208 | Schwisky | 1930.1771 | Amps | 300.7734 |  |  | HP0.95 | 572.7109
SUM | 0.70325 | Friction/OP. | 0.004189 | Tsurumi | 1579.8116 | Max. Output | 1225.1251 | 0.054567 | 0.60641 | HP1.5 | 22627.4163
IH/I | 0.0097794 | Total | 0.036861 | Thrust (1mm) | 313.9431 | % | 205.2824 |  |  | (RPM/1000)2.4 | 1.5489
|  | Efficiency | 0.96314 | Thrust (3 mm) | 610.2109 | Amps | 291.5937 |  |  | (RPM/1000)1.8 | 1.3884
Double Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 24
Slot Number | 42 | Slit Width | 8 | T.M.Wid.Low. | 17.5 | Watt Rad. | 0.11145 | Coil Cur. Density |  | k | 0.0685
Depth | 30.7 | Slit Depth | 3 | Cal.T.W.Up. | 0 | DG2L(cm2) | 100020.3876 | 4.57 / 4.71 |  | Hz | 60
Opening | 0 | L.S.Up.Wid. | 15.1546 | Cal.M.T.Wid. | 0 | GD2L(kg.m2) | 73.4993 | Bar Cur. Den. |  | Load Inertia | 7757.4956
Tip Depth | 0.7 | L.S.Low.Wid. | 11.7073 | Cal.M.T.Wid. | 17.5 | DO2L(cm2) | 219961 | UB: 4.01 / 4.13 | LB: -
Up. Sl. Wid. | 8 | L.S.Depth | 23 | X2S | 0 | IMC | 0.95 | ER Cur. Den.
Up. Sl. Dep. | 2 | T.M.Wid.Up. | 25.0914 | X3S | 0 | Coil Pitch Ct. | 0.9166 | UER: 1.79 / 1.84 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.39323 | 0.7 | 110.6523 | 593.2598
0.004 | 58.1513 | 79.2356 | 0.8 | 117.7369 | 609.1259
0.02 | 202.7784 | 281.7661 | 0.9 | 130.0449 | 625.1118
0.04 | 220 | 409.1365 | 1 | 150 | 640.3509
0.1 | 154.5346 | 464.3457
0.16 | 129.8628 | 493.0284 | Acceleration Data (FV V)
0.28 | 111.6962 | 524.2617 | Load Type: | Fan / Pump
0.4 | 105 | 544.4172 | Load Inertia: | 1307.6 kg.m²
0.5 | 105.2816 | 561.4147 | Accel. Time: | 9.6 (s)
0.6 | 106.9094 | 577.4471 | Rated Torque: | 490.3 kg.m
Load
100
99.2
95.25
89.75
74
58.8
36.4
22
14
8
6
8
15
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | 2T6800U | [5 empty] | HRW / Model Number: | 8006WTAL11E-A
Type: TIKK - Form: DCKW - 6 Pole - 800 HP - 4000 V - 60 Hz - 5811/12 - Class F | [9 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST | EPACT | M22 - 26Ga.
Material |  | NCB1 - 26Ga. |  | NL & Impedance Test | [5 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 1.6 |  | No load amps |  |  |  | 42 | - | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 620 |  | No load watts |  |  |  | 10857 | - | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 13 |  | Impedance amps |  | 3 | f | 232 | - | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.051"x.204")x1 |  | Impedance volts |  | 3 | f | 1150 | - | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | (.051"x.182")x1 |  | Impedance watts |  | 3 | f | 33812 | - | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [5 empty] | Dry Kiln
Connection |  | 2 x Wye |  |  | Winding |  | 80/115 | 77 / 102 | -
MCL |  | 1010 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 11.2896 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.5956 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 26 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 114
Coil grouping |  | - |  |  |  | RPM |  | 1180
Coil pitch (slot number) |  | 1 ~ 9 |  |  |  | CODE |  | H
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.1704 |  |  |  | DESIGN |  |  |  | Skip
Coil Weight | Wire1 | 177.6 |  |  |  | Nom.Eff. (%): |  |  |  | Adjacent
(lbs.) | Wire2 | 157.5 |  |  |  | Min.Eff. (%): |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | 80
FL / LR |  | 471 / 3012 | 413 / 184
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 729 | -
[6 empty] | LRT (%) | 60 | 149 | -
[6 empty] | BDT (%) | 175 | 219 | -
[6 empty] | SLIP (%) |  | 1.67 | -
[5 empty] | IEEE-B | Eff. (%) |  | 94.6 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 80 | -
|  |  |  | Losses (Watts) |  | Primary |  | 9021 | -
[6 empty] | Secondary |  | 7824 | -
[6 empty] | Core |  | 7400 | -
[6 empty] | F & W |  | 2500 | -
[6 empty] | Stray |  | 7172 | -
End Ring (Reference) |  |  |  | Note
LINK: 2N6800U.RAT & 2N6800U(EST).dat
THEN RUN 2N6800U REV1.RAT
Approved | A. Gracia | Design | Matt.O
Date | 2002-11-27 | Date | 2002-11-25 |  | REV1. CHG WIRE FROM 0.051"x0.204"x2
53.0
2.83
13.8
1800.0
450.0
55.0
35.0
340.0
0.70
30.70
2.0
5.0
8.0
15.15
23.00
11.71
Section
mm2
Section
mm2
M
M
311-
411-
350-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
CUSTOMER:
TIC SR No.:
MOTOR NAMEPLATE DATA
| H.P.: | 800 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1200
| FRAME: | 5812U |  | ENCL: | WP-II |  | FLAMPS: | 114 |  |  | FLRPM: | 1180
| FORM: | DCKW |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKK |  | AMB.: | 40 |  | CODE: | H |  |  | DUTY: | Cont.
| MODEL No.: | 8006WTAL11E-A |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 730 |  |  | FULL LOAD (lb-ft.): | 3561 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 150 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 220
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 94.6 | [5 empty] | FULL LOAD: | 80
|  | 3/4 LOAD: | 94.6 | [5 empty] | 3/4 LOAD: | 75.4
|  | 1/2 LOAD: | 93.9 | [5 empty] | 1/2 LOAD: | 65.3
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2022-11-01
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | 8006WTAL11E-A |  |  | FLAmps: | 114 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812U
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 800 | Rotor Inertia: | 436.0 lb-ft² | Date: | 2022-11-01
FLRPM: | 1180 | Load Inertia: | N/A | File: | 2T6800U REV1.
| Locked Rotor Amps: | 730 A | Load Type: | N/A
| Locked Rotor Torque: | 150% | Starting at: | N/A
| Breakdown Torque: | 220% | Accel. Time: | N/A
| Rated Torque: | 3561 lb-ft
Comments: | PROJECT | 0 |  | D.E.Curve #: | 2T6800U REV1.
|  | Prepared by: | JERRY R | Checked by:
100 | 0 | 0.39323
99.6 | 58.1513 | 79.2356
98 | 202.7784 | 281.7661
96 | 220 | 409.1365
90 | 154.5346 | 464.3457
84 | 129.8628 | 493.0284
72 | 111.6962 | 524.2617
60 | 105 | 544.4172
50 | 105.2816 | 561.4147
40 | 106.9094 | 577.4471
30 | 110.6523 | 593.2598
20 | 117.7369 | 609.1259
10 | 130.0449 | 625.1118
0 | 150 | 640.3509

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | 8006WTAL11E-A |  |  | FLAmps: | 114 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812U
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 800 | Rotor Inertia: | 436.0 lb-ft² | Date: | 2022-11-01
FLRPM: | 1180 | Load Inertia: | N/A | File: | 2T6800U REV1.
Comments: | PROJECT | 0 |  | D.E.Curve #: | 2T6800U REV1.
|  | Prepared by: | JERRY R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
640.3509 | 13.0886 | 5.4838 |  | 640.3509 | 0.0001
600 | 14.9082 | 6.2462 |  | 632.7193 | 0.767
500 | 21.4678 | 8.9946 |  | 617.1053 | 1.569
400 | 33.5435 | 14.054 |  | 601.2281 | 2.41
300 | 59.6328 |  |  | 585.3509 | 3.295
200 | 134.1738 |  |  | 569.4737 | 4.243
220 | 110.8875 | 46.4595 |  | 552.8947 | 5.278
180 | 188.6758 | 69.4025 |  | 534.2982 | 6.645
145 | 255.2653 | 106.9508 |  | 508.6842 | 8.123
125 |  | 300 |  | 478.6842 | 8.836
125 |  | 600 |  | 436.7544 | 9.349
125 |  | 10000 |  | 345.4386 | 9.501
|  |  |  | 0 | 9.633

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 8006WTAL11E-A |  |  | FLAmps: | 114 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812U
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 800 | Rotor Inertia: | 436.0 lb-ft² | Date: | 2022-11-01
FLRPM: | 1180 | Load Inertia: | N/A | File: | 2T6800U REV1.
| Locked Rotor Amps: | 730 A | Load Type: | N/A
| Locked Rotor Torque: | 150% | Starting at: | N/A
| Breakdown Torque: | 220% | Accel. Time: | N/A
| Rated Torque: | 3561 lb-ft
Comments: | PROJECT | 0 |  | D.E.Curve #: | 2T6800U REV1.
|  | Prepared by: | JERRY R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 46.2811 | 100 | 11.1664
25 | 91.0254 | 42.8723 | 55.2504 | 69.6586 | 10.2565
50 | 93.9165 | 65.2833 | 70.3333 | 57.9739 | 19.8816
75 | 94.5504 | 75.4449 | 90.6783 | 45.9535 | 29.6225
100 | 94.5816 | 79.9897 | 113.9972 | 33.5013 | 39.4836
125 | 94.3586 | 81.8371 | 139.6091 | 20.748 | 49.4711
1200
1197
1194
1191
1188
1185
1182
1179
1176
1173
1170
RPM
1600
800
640
480
320
160
Input Watts (kW)
960
1120
1280
1440
EFF.
P.F.
RPM
AMPS
WATTS
0

## StallTime
Rating: | 6 Pole - 800.0 HP - 1200 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 7757.5 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~120 | 140.0 | 22.5 | 0.767 | 721.3 | 278.7 | 620.4
120~240 | 123.9 | 11.5 | 0.802 | 703.5 | 277.7 | 506.0
240~360 | 114.2 | 7.0 | 0.841 | 685.4 | 276.4 | 427.0
360~480 | 108.8 | 7.0 | 0.885 | 667.3 | 276.1 | 369.8
480~600 | 106.1 | 11.0 | 0.948 | 649.2 | 280.0 | 327.8
600~720 | 105.1 | 18.0 | 1.035 | 630.3 | 289.0 | 293.7
720~864 | 108.3 | 29.2 | 1.367 | 609.1 | 359.1 | 258.0
864~1008 | 120.8 | 47.6 | 1.478 | 579.9 | 359.9 | 207.6
1008~1080 | 142.2 | 66.4 | 0.713 | 545.7 | 153.7 | 133.2
1080~1152 | 187.3 | 81.9 | 0.513 | 497.9 | 98.0 | 71.3
1152~1176 | 211.4 | 92.5 | 0.152 | 393.8 | 22.5 | 36.0
1176~1186 | 151.4 | 97.2 | 0.132 | 205.8 | 1.2 | 22.0
Acceleration Time: 9.6 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2672 kW / s |  | 46°C |  | 91°C
Rotor Bar Rise | 2972 kW / s |  | 134°C |  | 267°C
End Ring Rise | 301 kW / s |  | 27°C |  | 53°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 7.4°C / s |  | 436.2 kW | 160°C | 21.5 s
Rotor Bar | 36.6°C / s |  | 812.8 kW | 260°C | 7.1 s
Rotor ER | 7.2°C / s |  | 82.4 kW | 180°C | 24.8 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 77°C + |  | 83°C + | 40°C | = 200°C | 11.2 s
Rotor Bar | 105°C + |  | 155°C + | 40°C | = 300°C | 4.2 s
Rotor ER | 105°C + |  | 75°C + | 40°C | = 220°C | 10.4 s
Cold Stall Time: | 9.2 s |  | Hot Stall Time: |  | 3.8 s