## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RATFILE\DT2700K_Rev1.rat |  |  |  |  | Date: | 2019-04-23 | Time: | 11:23
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 700 | 3600 | DCKW | 4000 | 60 | 105 | 3578.1 / 3575.0 | 0.0061 / 0.0069 | 5011/12
Core Data |  |  | Winding Data | USA Wire Std |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 25.4319 | LR Test Data
Air Gap | 2.9 | [5 empty] | Rt. Slot Pitch | 30.88 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 14 | Cross Section Area |  | Mean Value | 28.156 | 641.7043
Core Length | 452 | 452 |  |  | UB: 304.0 | UER: 1750.0 | Eff.T.W.St. | 18.2475 | WS
OD | 590 | 334.2 | Coil Pitch | 0.61899 |  |  | Eff.T.W.Rt. | 30.4083 | 26458.4971
ID | 340 | 155 | Slot Fill | - | EBL: 40.0 | ERD1: 211.4 | St.Carter Fac. | 1.3937 | IS
Core Depth | 68 | 53.19 | Con./Slot | 18 |  | ERT: 70.00 | Rt.Carter Fac. | 1.0155 | 86.3678
Eff.Core L. | 353.4 | 360.84 | Wire Size 1 | (.081"x.182")x1 |  | ERH: 25.00 | Carter Factor | 1.4153 | Volts / Turn
Slot Data |  |  | Wire Size 2 | (.081"x.204")x1 |  |  | Short. Factor | 0.82618 | 18.3291
Number | 42 | 34 | // Circuits | 1 |  |  | Distrib. Factor | 0.95565 | AC
Kind | Open | Trapeze | Connection | Wye |  |  | Wind. Factor | 0.78954 | 611.2868
Skew | - | 0 | MCL | 1071 | 602 |  | Reactance | (Coeff.: 0.0702)
Depth | 57 | 36.41 | No.Cond./Ph. | 252 |  |  |  | Running | Start
Width | 14.00 - 14.00 |  | Res. (20°C) | 0.24044 |  |  | Stator Slot | 11.786 | 11.786
Opening | 14 | 3 | (105°C) | 0.32075 | 0.16247 | 0.018251 | Rotor Slot | 16.4334 | 14.4689
Tip Depth | 2.83 | 3 | Material | CU | Special | Special | Zigzag | 6.768 | 6.0389
T.Min.Wid. | 11.4319 | 10.0314 | Spec.Resist. | 1.742 | 1.724 | 1.724 | Coil End | 21.3241 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 5.7711 | 5.1494
Up. R. | - | 4.72 | Weight (kg) |  |  |  | Total Resist. | 0.50147 | 1.1823
Wedge Dep. | 1.20 - 2.40 | Normal | Wire 1 | 66.2356 | 61.7481 | 23.1063 | Total React. | 4.3563 | 4.1236
Duct | 9 x 8 | 8 x 8 | Wire 2 | 74.511 | - | - | Impedance | 4.385 | 4.2898
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 33.3714 |  | Length | Section | Density | AT | Volume | Loss |  | 3569.4 | 125RPM
| Reac.= | 33.399 | Primary Core | 46.3385 | 480.624 | 18.1313 | 929.5391 | 39409.004 | 3666.1741 |  | 3575.0 | 100RPM
Excitation Data |  |  | Tooth | 5.7 | 848.4084 | 10.2714 | 14.8277 | 9671.8561 | 358.354 |  | 3580.5 | 75RPM
Excit.Amps | 24.184 / 19.479 |  | Second.Core | 20.5287 | 570.2956 | 15.2804 | 201.23 | Total | 4024.528 |  | 3586.0 | 50RPM
Core Loss | 1.114 / 0.898 | Flux / Pole | Tooth | 3.641 | 615.3563 | 14.1614 | 25.9376 | C.L.C. | 1.50 / 0.77 |  | 3591.4 | 25RPM
NoLoad | 24.21 / 19.50 | 8.7143 | Air Gap | 0.29 | 1449.0003 | 6.014 | 1387.8856 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 48 / 48 |  | No Load Loss | 11150.9 / 10500.0 | W.Loss | 6036.8 / 3099.7
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 7177.8 / 6632.2 | S.Loss | 1692.2 / 868.9
Current (A) | 33.30 / 34.00 | 48.42 / 49.44 | 66.67 / 68.06 | 86.37 / 88.18 | 107.08 / 109.33 | Second. Loss | 3283.2 / 3718.1 | Total C.Loss | 7729.0 / 3968.6
Efficiency | 0.916 / 0.909 | 0.950 / 0.943 | 0.959 / 0.952 | 0.962 / 0.954 | 0.961 / 0.953 | Frict.& Wind. | 3000.0 / 6254.5 | Stray Loss | 4642.8994 | 0.962 | 0.954 | 0.99168 | Eff.
P.F. | 0.618 / 0.610 | 0.819 / 0.809 | 0.884 / 0.873 | 0.9076 / 0.8960 | 0.916 / 0.904 | Starting Data |  | Slip | PF | 0.9076 | 0.8960 | 0.98722 | PF.
Slip | 0.0015 / 0.0024 | 0.0030 / 0.0039 | 0.0045 / 0.0054 | 0.0061 / 0.0069 | 0.0077 / 0.0085 | LRA | 538.4 / 465.3 |  |  | 86.37 | 88.18 | 1.021 | Current
RPM | 3594.5 / 3591.4 | 3589.1 / 3586.0 | 3583.6 / 3580.5 | 3578.1 / 3575.0 | 3572.4 / 3569.4 | % | 623.3 / 538.7 |  |  | 3578.1 | 3575.0 | 0.99913 | RPM
L (Inv., MH) | 9.9662 | 9.9662 | 9.9662 | 9.9662 | 9.9662 | LRT (kg.m) | 203.1 / 126.4 |  | 0.27562
(No Load) | 9.9662 |  | Correlated to: LAB 0775.dat |  |  | % | 142.9 / 88.9
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1629.3422 | 0.041374 | 0.62475
IM/IW | 0.31078 | I*R1/E | 0.011885 | Rosenberg | 326.2355 | % | 310.1 / 277.7
IW*X/E | 0.14678 | I*R2/E | 0.0060895 | Schwisky | 511.3273 | Amps | 360.8457 |  |  | HP0.95 | 504.4791
SUM | 0.45756 | Friction/OP. | 0.0057449 | Tsurumi | 185.1431 | Max. Output | 1563.4218 | 0.039582 | 0.63963 | HP1.5 | 18520.2592
IH/I | 0.013023 | Total | 0.036742 | Thrust (1mm) | 82.5171 | % | 299.3914 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.96326 | Thrust (3 mm) | 200.1765 | Amps | 352.7859 |  |  | (RPM/1000)1.8 | 10.031
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 34 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.10977 | Coil Cur. Density |  | k | 0.0685
Depth | 36.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 43335.5803 | 4.42 / 4.51 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 19.3605 | Bar Cur. Den. |  | Load Inertia | 503.1518
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 132278 | UB: 4.49 / 4.59 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.67848 | UER: 4.23 / 4.32 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.27511 | 0.69716 | 87.1023 | 520.3431
0.0082 | 129.7244 | 123.7272 | 0.79811 | 86.0078 | 523.3902
0.041 | 275 | 386.8932 | 0.89905 | 85.3621 | 526.0626
0.091474 | 182.3007 | 465.4197 | 1 | 85 | 528.4091
0.14195 | 137.4974 | 487.2974
0.19242 | 116.4611 | 496.1664 | Acceleration Data (FV V)
0.29337 | 103.0288 | 504.0313 | Load Type: | Fan / Pump
0.39432 | 96.0839 | 508.846 | Load Inertia: | 84.8 kg.m²
0.49526 | 91.7132 | 513.0486 | Accel. Time: | 9.2 (s)
0.59621 | 88.8889 | 516.8922 | Rated Torque: | 142.1 kg.m
DesPro8AX Draft
Load
100
98.36
89.475
76.2168
63.0937
51.6674
34.1274
22.6253
14.3789
8.2274
6.0568
7.9621
14.9337
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | DT2700K_Rev1 | [5 empty] | HRW / Model Number: | 7003WTQK11F-C
Type: TIKE - Form: DCKW - 2 Pole - 700 HP - 2300 / 4000 V - 60 Hz - 5011/12 - Class F | [11 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  |  | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [7 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 2.9 |  | No load amps |  |  |  | 34 / 19.5 | - |  |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 452 |  | No load watts |  |  |  | 10500 | - |  |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 9 |  | Impedance amps |  | 3 | f | 155 | - |  |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.081"x.182")x1 |  | Impedance volts |  | 3 | f | 1150 | - |  |  | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | (.081"x.204")x1 |  | Impedance watts |  | 3 | f | 26459 | - |  |  | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 1D / 1Y |  |  | Winding |  | 80/115 | 48 / 63 | -
MCL |  | 1071 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 13.5368 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7956 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 18 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 152 / 88
Coil grouping |  | - |  |  |  | RPM |  | 3575
Coil pitch (slot number) |  | 1 ~ 14 |  |  |  | CODE |  | E
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.2404 |  |  |  | DESIGN |  | - |  |  |  | Skip
Coil Weight | Wire1 | 145.7 |  |  |  | Nom.Eff. (%): |  | - |  |  |  | Adjacent
(lbs.) | Wire2 | 163.9 |  |  |  | Min.Eff. (%): |  | - |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 451 / 2383 | 459 / 432
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 805/ 465 | - | 528.4% | 529.6%
[6 empty] | LRT (%) | 60 | 88 | -
[6 empty] | BDT (%) | 175 | 277 | -
[6 empty] | SLIP (%) |  | 0.69 | -
[5 empty] | IEEE-B | Eff. (%) |  | 95.4 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 89.6 | -
|  |  |  | Losses (Watts) |  | Primary |  | 6632 | -
[6 empty] | Secondary |  | 3718 | -
[6 empty] | Core |  | 3969 | -
[6 empty] | F & W |  | 6255 | -
[6 empty] | Stray |  | 4643 | -
End Ring (Reference) |  |  |  | Note | 7003WTQK11F-C
|  |  |  | LINK: | DT2700K_Rev1.rat with LAB 0775.dat
Approved |  | Design | W.McDaniel
Date |  | Date | 2005-07-20 |  | REV.1 Update Correleration. Z.X 04/23/2019
261.4
25.0
40.0
70.0
M
36.41
3.00
3.00
14.12
4.72
57.0
2.83
14.0
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 2 Pole - 700.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 503.2 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~363 | 85.2 | 22.5 | 1.133 | 464.0 | 235.7 | 503.6
363~727 | 85.7 | 11.4 | 0.957 | 461.8 | 197.4 | 384.2
727~1090 | 86.6 | 7.0 | 0.893 | 459.2 | 182.4 | 320.7
1090~1454 | 88.0 | 7.1 | 0.878 | 456.4 | 177.1 | 278.8
1454~1817 | 90.3 | 11.3 | 0.899 | 453.2 | 179.0 | 249.2
1817~2180 | 93.9 | 18.5 | 0.942 | 449.6 | 184.8 | 223.8
2180~2544 | 99.6 | 28.4 | 0.998 | 445.7 | 192.5 | 197.7
2544~2907 | 109.7 | 42.9 | 1.063 | 440.1 | 201.3 | 168.1
2907~3089 | 127.0 | 57.4 | 0.510 | 432.7 | 93.6 | 119.6
3089~3271 | 159.9 | 69.7 | 0.394 | 419.2 | 69.7 | 80.4
3271~3452 | 228.7 | 82.8 | 0.244 | 375.0 | 39.3 | 42.5
3452~3570 | 202.4 | 93.9 | 0.213 | 224.7 | 23.7 | 38.6
3570~3578 | 114.9 | 99.2 | 0.095 | 65.1 | 0.7 | 18.7
Acceleration Time: 9.2 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 1777 kW / s |  | 33°C |  | 66°C
Rotor Bar Rise | 2361 kW / s |  | 99°C |  | 199°C
End Ring Rise | 265 kW / s |  | 30°C |  | 60°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 4.4°C / s |  | 238.5 kW | 160°C | 36.3 s
Rotor Bar | 16.8°C / s |  | 399.0 kW | 260°C | 15.5 s
Rotor ER | 5.0°C / s |  | 44.8 kW | 180°C | 35.7 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 63°C + |  | 97°C + | 40°C | = 200°C | 22.0 s
Rotor Bar | 83°C + |  | 177°C + | 40°C | = 300°C | 10.5 s
Rotor ER | 83°C + |  | 97°C + | 40°C | = 220°C | 19.2 s
Cold Stall Time: | 26.9 s |  | Hot Stall Time: |  | 14.5 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | -
| TIC SR No.: | -
MOTOR NAMEPLATE DATA
| H.P.: | 700 |  | VOLTS: | 2300/4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5011/12 |  | ENCL: | WP-II |  | FLAMPS: | 152/88 |  |  | FLRPM: | 3575
| FORM: | DCKW |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | E |  |  | DUTY: | Cont.
| MODEL No.: | 7003WTQK11F-C |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 805/465 |  |  | FULL LOAD (lb-ft.): | 1028 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 85 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 275
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.4 | [5 empty] | FULL LOAD: | 89.6
|  | 3/4 LOAD: | 95.1 | [5 empty] | 3/4 LOAD: | 87.3
|  | 1/2 LOAD: | 94.2 | [5 empty] | 1/2 LOAD: | 80.9
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2019-04-23
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | 7003WTQK11F-C |  |  | FLAmps: | 152/88
Enclosure: | WP-II | Voltage: | 2300/4000 V | Frame: | 5011/12
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 114.9 lb-ft² | Date: | 2019-04-23
FLRPM: | 3575 | Load Inertia: | 503.2 lb-ft² | File: | DT2700K
| Locked Rotor Amps: | 805/465 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 85% | Starting at: | FV (V)
| Breakdown Torque: | 275% | Accel. Time: | 9.2 (s)
| Rated Torque: | 1028 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | DT2700K
|  | Prepared by: | Zichao Xie | Checked by:
Load
100 | 0 | 0.27511 | 100
99.18 | 129.7244 | 123.7272 | 98.36
95.9 | 275 | 386.8932 | 89.475
90.8526 | 182.3007 | 465.4197 | 76.2168
85.8053 | 137.4974 | 487.2974 | 63.0937
80.7579 | 116.4611 | 496.1664 | 51.6674
70.6632 | 103.0288 | 504.0313 | 34.1274
60.5684 | 96.0839 | 508.846 | 22.6253
50.4737 | 91.7132 | 513.0486 | 14.3789
40.3789 | 88.8889 | 516.8922 | 8.2274
30.2842 | 87.1023 | 520.3431 | 6.0568
20.1895 | 86.0078 | 523.3902 | 7.9621
10.0947 | 85.3621 | 526.0626 | 14.9337
0 | 85 | 528.4091 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | 7003WTQK11F-C |  |  | FLAmps: | 152/88
Enclosure: | WP-II | Voltage: | 2300/4000 V | Frame: | 5011/12
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 114.9 lb-ft² | Date: | 2019-04-23
FLRPM: | 3575 | Load Inertia: | 503.2 lb-ft² | File: | DT2700K
805/465 A
85%
1028 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | DT2700K
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
528.4091 | 35 | 15 |  | 528.4091 | 0.0001
492.9429 | 40.2175 | 17.2361 |  | 527.2727 | 1.133
457.4661 | 46.6972 | 20.0131 |  | 524.7727 | 2.09
422 | 54.8762 | 23.5184 |  | 521.8182 | 2.983
322 | 94.2534 |  |  | 518.6364 | 3.861
222 | 198.2908 |  |  | 515 | 4.76
275 | 129.224 | 55.3817 |  | 510.9091 | 5.702
180 | 346.5859 | 129.2667 |  | 506.4773 | 6.7
145 | 464.8069 | 199.203 |  | 500.1136 | 7.763
125 |  | 400 |  | 491.7045 | 8.273
125 |  | 800 |  | 476.3636 | 8.667
125 |  | 10000 |  | 426.1364 | 8.911
|  |  |  | 125 | 9.124
|  |  |  | 0 | 9.219

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 7003WTQK11F-C |  |  | FLAmps: | 152/88
Enclosure: | WP-II | Voltage: | 2300/4000 V | Frame: | 5011/12
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 114.9 lb-ft² | Date: | 2019-04-23
FLRPM: | 3575 | Load Inertia: | 503.2 lb-ft² | File: | DT2700K
| Locked Rotor Amps: | 805/465 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 85% | Starting at: | FV (V)
| Breakdown Torque: | 275% | Accel. Time: | 9.2 (s)
| Rated Torque: | 1028 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | DT2700K
|  | Prepared by: | Zichao Xie | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 24.7179 | 100 | 0.75
25 | 90.8455 | 60.9768 | 34.0003 | 82.5009 | 10.2595
50 | 94.2225 | 80.865 | 49.4385 | 71.7544 | 19.7836
75 | 95.1226 | 87.2688 | 68.0658 | 60.7929 | 29.3946
100 | 95.3525 | 89.5985 | 88.1815 | 49.7154 | 39.0983
125 | 95.3018 | 90.3843 | 109.3268 | 38.4365 | 48.8989
3600
3595
3590
3585
3580
3575
3570
3565
3560
3555
3550
RPM
1400
700
560
420
280
140
Input Watts (kW)
840
980
1120
1260
EFF.
P.F.
RPM
AMPS
WATTS
0