## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | M:\Active Projects\6810 Development\Electrical Design\2P\SERIES\DT2C20U.rat |  |  |  |  | Date: | 2014-08-20 | Time: | 14:57
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 5000 | 3600 | DCW4 | 4000 | 60 | 105 | 3579.9 / 3586.9 | 0.0056 / 0.0036 | 450-1600
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 26.1799 | LR Test Data
Air Gap | 3.5 | [5 empty] | Rt. Slot Pitch | 30.2549 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 18 | Cross Section Area |  | Mean Value | 28.2174 | 200.1647
Core Length | 1030 | 1030 |  |  | UB: 322.1 | UER: 3768.4 | Eff.T.W.St. | 17.1276 | WS
OD | 815 | 443 | Coil Pitch | 0.62957 |  |  | Eff.T.W.Rt. | 29.8593 | 130878.6534
ID | 450 | 170 | Slot Fill | - | EBL: 62.5 | ERD1: 328.0 | St.Carter Fac. | 1.5285 | IS
Core Depth | 109.5 | 98.09 | Con./Slot | 14 |  | ERT: 65.54 | Rt.Carter Fac. | 1.0132 | 586.4795
Eff.Core L. | 790.5 | 846.3 | Wire Size 1 | (.128"x.258")x2 |  | ERH: 57.50 | Carter Factor | 1.5488 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.83543 | 63.4921
Number | 54 | 46 | // Circuits | 2 |  |  | Distrib. Factor | 0.95529 | AC
Kind | Open | Trapeze | Connection | Delta |  |  | Wind. Factor | 0.79808 | 905.3879
Skew | - | 0 | MCL | 1917 | 1220.537 |  | Reactance | (Coeff.: 0.0312)
Depth | 73 | 38.41 | No.Cond./Ph. | 126 |  |  |  | Running | Start
Width | 17.30 - 17.30 |  | Res. (20°C) | 0.050679 |  |  | Stator Slot | 14.9933 | 14.9933
Opening | 17.3 | 3 | (105°C) | 0.067605 | 0.05922 | 0.010817 | Rotor Slot | 16.3182 | 13.7978
Tip Depth | 13.15 | 3 | Material | CU | CU | CU | Zigzag | 4.6908 | 3.6925
T.Min.Wid. | 8.8799 | 10.8884 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 17.6321 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 6.7858 | 5.3803
Up. R. | - | 5.72 | Weight (kg) |  |  |  | Total Resist. | 0.13764 | 0.38049
Wedge Dep. | 0.80 - 2.40 | Normal | Wire 1 | 534.8443 | 169.4222 | 84.5315 | Total React. | 1.8871 | 1.7321
Duct | 30 x 6 | 20 x 6 | Wire 2 | - | - | - | Impedance | 1.8921 | 1.7734
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.3592 |  | Length | Section | Density | AT | Volume | Loss
| Reac.= | 35.3955 | Primary Core | 64.0099 | 1731.195 | 17.2501 | 1047.3859 | 191850.3153 | 16463.7251
Excitation Data |  |  | Tooth | 7.3 | 1895.2851 | 15.7566 | 81.5618 | 27671.1627 | 2050.5989
Excit.Amps | 63.935 / 70.583 |  | Second.Core | 28.7597 | 2139.8413 | 13.9558 | 193.0972 | Total | 18514.324
Core Loss | 3.762 / 4.153 | Flux / Pole | Tooth | 3.841 | 2119.4204 | 14.0903 | 26.8069 | C.L.C. | 1.75 / 0.74
NoLoad | 110.93 / 122.46 | 29.8633 | Air Gap | 0.35 | 4016.3051 | 7.4355 | 2070.947 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 60 / 61 |  | No Load Loss | 56505.4 / 50969.5 | W.Loss | 32400.1 / 13763.3
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 23254.8 / 23515.1 | S.Loss | 12783.9 / 5430.5
Current (A) | 187.50 / 192.85 | 309.51 / 318.35 | 444.97 / 457.68 | 586.48 / 603.22 | 732.99 / 753.92 | Second. Loss | 21322.1 / 13481.1 | Total C.Loss | 45183.9 / 19193.8
Efficiency | 0.940 / 0.935 | 0.965 / 0.960 | 0.972 / 0.967 | 0.974 / 0.969 | 0.974 / 0.969 | Frict.& Wind. | 10700.0 / 28349.0 | Stray Loss | 33736.4922
P.F. | 0.764 / 0.746 | 0.901 / 0.880 | 0.934 / 0.912 | 0.942 / 0.921 | 0.942 / 0.921 | Starting Data |  | Slip | PF
Slip | 0.0014 / -0.0006 | 0.0028 / 0.0008 | 0.0041 / 0.0022 | 0.0056 / 0.0036 | 0.0070 / 0.0050 | LRA | 3906.6 / 3719.7
RPM | 3595.0 / 3602.0 | 3590.1 / 3597.1 | 3585.1 / 3592.0 | 3579.9 / 3586.9 | 3574.9 / 3581.8 | % | 666.1 / 634.2
L (Inv., MH) | 4.2465 | 4.2465 | 4.2465 | 4.2465 | 4.2465 | LRT (kg.m) | 1294.6 / 1596.2 |  | 0.21456
(No Load) | 4.2465 |  | Correlated to: H402129_Lab#1565_byRM.dat |  |  | % | 127.6 / 157.3
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 11903.0518 | 0.03709 | 0.64898
IM/IW | 0.2007 | I*R1/E | 0.0057165 | Rosenberg | 1476.3545 | % | 317.3 / 236.2
IW*X/E | 0.15029 | I*R2/E | 0.0055778 | Schwisky | 2114.6165 | Amps | 2549.1202
SUM | 0.35099 | Friction/OP. | 0.0028686 | Tsurumi | 716.8521 | Max. Output | 11470.0378 | 0.035694 | 0.66227
IH/I | 0.011121 | Total | 0.025284 | Thrust (1mm) | 478.2065 | % | 307.5077
|  | Efficiency | 0.97472 | Thrust (3 mm) | 1219.5076 | Amps | 2499.8086
Single Cage Data | [5 empty] | Miscellaneous Data
Slot Number | 46 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.12151 | Coil Cur. Density
Depth | 38.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 178586.59 | 4.08 / 4.19
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 140.1898 | Bar Cur. Den.
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 564591.25 | UB: 6.49 / 6.67 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.69435 | UER: 4.06 / 4.18 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.18396 | 0.68737 | 157.017 | 607.5301
0.002 | 120.0302 | 152.5878 | 0.79158 | 157.0064 | 611.1486
0.01 | 236 | 463.9668 | 0.89579 | 157.0043 | 614.2423
0.062105 | 179.2503 | 544.881 | 1 | 157 | 616.9154
0.11421 | 162.9134 | 566.6228
0.16632 | 158.2386 | 575.7802 | Acceleration Data (FV V)
0.27053 | 157.1005 | 585.6714 | Load Type: | Fan / Pump
0.37474 | 157.0678 | 592.4611 | Load Inertia: | 280.2 kg.m²
0.47895 | 157.0498 | 598.27 | Accel. Time: | 3.2 (s)
0.58316 | 157.0336 | 603.2715 | Rated Torque: | 1014.8 kg.m
Load
100
99.6
98
83.8526
70.3053
57.4105
38.0105
24.7789
15.6842
9.0105
6.2526
7.8316
14.7053
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | DT2C20U | [5 empty] | HRW / Model Number: | C203WTQL11F-C
Type: TIKE - Form: DCW4 - 2 Pole - 5000 HP - 4000 V - 60 Hz - 450-1600 - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M36 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 3.5 |  | No load amps |  |  |  | 123 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 1030 |  | No load watts |  |  |  | 48360 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 7 |  | Impedance amps |  | 3 | f | 3369 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.128"x.258")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  | OWP | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 130879 | - |  | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 2 x Delta |  |  | Winding |  | 80/115 | 60 / 79 | -
MCL |  | 1917 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 11.5332 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7936 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 14 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 603 |  | 3919.5
Coil grouping |  | - |  |  |  | RPM |  | 3587
Coil pitch (slot number) |  | 1 ~ 18 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.054 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 1210 |  |  |  | Nom.Eff. (%): |  | - |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 419 / 2585 | 667 / 418
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 3720 | - | 616.9154
[6 empty] | LRT (%) | 60 | 157 | -
[6 empty] | BDT (%) | 175 | 236 | -
[6 empty] | SLIP (%) |  | 0.36 | -
[5 empty] | IEEE-B | Eff. (%) |  | 96.9 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 92.1 | -
|  |  |  | Losses (Watts) |  | Primary |  | 23515 | -
[6 empty] | Secondary |  | 13481 | -
[6 empty] | Core |  | 19194 | -
[6 empty] | F & W |  | 28349 | -
[6 empty] | Stray |  | 33736 | -
End Ring (Reference) |  |  |  | Note
|  |  |  | LINK: | H402129.rat with H402129_Lab#1565_byRM.dat
Run DT2C20U.rat
QC Limits: DT2C20U
Approved | S.Hernandez | Design | A.Gracia
Date | 2014-08-22 | Date | 2014-08-20
38.41
3.00
3.00
14.12
5.72
73.0
13.15
17.3
051-TB13
328.0
62.5
85.0
57.5
18.50
55
.0
411-TC13
311-TC13
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## Form
Winding Data Calculation
MCL: 1917.0
Coil Resistance |  |  | Lead Resistance
7T: | 0.0114 ~ 0.0109 |  | AWG. 1/0 x 3
0.00142
Coil Dimensions
HM: | 7T: 24.16 | WM: | 7T: 13.51 | WT:
17.40 ~ 17.00
Insulation Allowance |  |  | Wire Weight
Depth: | 11.53 |  | (.128"x.258")x 2: |  | 1210 lbs.
Width: | 3.79
QC Resistance
1-2, 2-3, 3-1: |  | 0.037 ~ 0.035

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | C203WTQL11F-C |  |  | FLAmps: | 603
Enclosure: | DCW4 | Voltage: | 4000 V | Frame: | 450-1600
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 5000 | Rotor Inertia: | 831.7 lb-ft² | Date: | 2014-08-20
FLRPM: | 3587 | Load Inertia: | N/A | File: | DT2C20U
| Locked Rotor Amps: | 3720 A | Load Type: | N/A
| Locked Rotor Torque: | 157% | Starting at: | N/A
| Breakdown Torque: | 236% | Accel. Time: | N/A
| Rated Torque: | 7325 lb-ft
Comments: |  |  |  | D.E.Curve #:
|  | Prepared by: | AG | Checked by: | SH
Load
100 | 0 | 0.18396 | 100
99.8 | 120.0302 | 152.5878 | 99.6
99 | 236 | 463.9668 | 98
93.7895 | 179.2503 | 544.881 | 83.8526
88.5789 | 162.9134 | 566.6228 | 70.3053
83.3684 | 158.2386 | 575.7802 | 57.4105
72.9474 | 157.1005 | 585.6714 | 38.0105
62.5263 | 157.0678 | 592.4611 | 24.7789
52.1053 | 157.0498 | 598.27 | 15.6842
41.6842 | 157.0336 | 603.2715 | 9.0105
31.2632 | 157.017 | 607.5301 | 6.2526
20.8421 | 157.0064 | 611.1486 | 7.8316
10.4211 | 157.0043 | 614.2423 | 14.7053
0 | 157 | 616.9154 | 30

## StallTime
Rating: | 2 Pole - 5000.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 1662.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~375 | 157.0 | 22.4 | 0.308 | 3711.9 | 288.0 | 1965.9
375~750 | 157.0 | 11.3 | 0.284 | 3694.6 | 263.8 | 1626.9
750~1125 | 157.0 | 7.0 | 0.276 | 3674.3 | 253.6 | 1396.4
1125~1501 | 157.0 | 7.6 | 0.277 | 3650.6 | 251.6 | 1217.5
1501~1876 | 157.0 | 12.3 | 0.286 | 3622.6 | 256.2 | 1066.6
1876~2251 | 157.1 | 20.2 | 0.303 | 3590.1 | 266.5 | 926.7
2251~2626 | 157.1 | 31.4 | 0.330 | 3552.1 | 284.4 | 789.2
2626~3001 | 157.7 | 47.7 | 0.377 | 3501.8 | 317.6 | 651.2
3001~3189 | 160.6 | 63.9 | 0.214 | 3444.3 | 174.6 | 458.7
3189~3376 | 171.1 | 77.1 | 0.220 | 3351.2 | 174.0 | 333.6
3376~3564 | 207.6 | 90.9 | 0.178 | 3041.7 | 129.6 | 160.8
3564~3593 | 178.0 | 98.8 | 0.040 | 1858.9 | 21.3 | 50.2
3593~3600 | 110.0 | 99.8 | 0.078 | 794.5 | 1.9 | 110.6
Acceleration Time: 3.2 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2683 kW / s |  | 13°C |  | 26°C
Rotor Bar Rise | 9093 kW / s |  | 139°C |  | 279°C
End Ring Rise | 1661 kW / s |  | 51°C |  | 102°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 5.2°C / s |  | 1065.3 kW | 160°C | 30.9 s
Rotor Bar | 75.9°C / s |  | 4951.6 kW | 260°C | 3.4 s
Rotor ER | 27.8°C / s |  | 904.5 kW | 180°C | 6.5 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 61°C + |  | 99°C + | 40°C | = 200°C | 19.1 s
Rotor Bar | 80°C + |  | 180°C + | 40°C | = 300°C | 2.4 s
Rotor ER | 80°C + |  | 100°C + | 40°C | = 220°C | 3.6 s
Cold Stall Time: | 10.6 s |  | Hot Stall Time: |  | 5.9 s

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | C203WTQL11F-C |  |  | FLAmps: | 603
Enclosure: | DCW4 | Voltage: | 4000 V | Frame: | 450-1600
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 5000 | Rotor Inertia: | 831.7 lb-ft² | Date: | 2014-08-20
FLRPM: | 3587 | Load Inertia: | 1662.0 lb-ft² | File: | DT2C20U
Comments: |  |  |  | D.E.Curve #:
|  | Prepared by: | AG | Checked by: | SH
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
616.9154 | 15.1483 | 8.4151 |  | 616.9154 | 0.0001
600 | 16.0145 | 8.8963 |  | 615.5721 | 0.308
500 | 23.0609 | 12.8107 |  | 612.7032 | 0.592
400 | 36.0326 | 20.0167 |  | 609.3367 | 0.868
300 | 64.058 |  |  | 605.4063 | 1.145
200 | 144.1306 |  |  | 600.7629 | 1.431
236 | 103.5123 | 57.5027 |  | 595.3731 | 1.734
180 | 188.1134 | 98.8478 |  | 589.0713 | 2.064
120 | 400.3627 | 222.4076 |  | 580.7297 | 2.441
110 |  | 500 |  | 571.194 | 2.655
110 |  | 1000 |  | 555.7546 | 2.875
110 |  | 10000 |  | 504.4279 | 3.053
|  |  |  | 308.2753 | 3.093
|  |  |  | 0 | 3.171

## MagNoise
Magnetic Noise Verification
Rating: | 2 Pole - 5000.0 HP - 3600 RPM - 4000 V - 60 Hz
Electromagnetic Excitation Frequencies
| L = | 0 | L = | + 1 | L = | - 1 | Slip = | 0 | Slip = | 0.006
Mode A | 6 |  | 12 |  | 0 |  | 2880.0 Hz |  | 2864.6 Hz
Mode B | 10 |  | 16 |  | 4 |  | 2640.0 Hz |  | 2624.6 Hz
Mode C | 8 |  | 14 |  | 2 |  | 2760.0 Hz |  | 2744.6 Hz
Natural Frequencies of Stator Core
| Mode 0 = |  | 1483.0 Hz |  | Mode 6 = |  | 4554.3 Hz
| Mode 2 = |  | 354.0 Hz |  | Mode 7 = |  | 6268.4 Hz
| Mode 3 = |  | 1001.2 Hz |  | Mode 8 = |  | 8246.6 Hz
| Mode 4 = |  | 1919.7 Hz |  | Mode 9 = |  | 10488.8 Hz
| Mode 5 = |  | 3104.5 Hz |  | Mode 10 = |  | 12995.0 Hz
Analysis Results
No matching frequencies detected.

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | -
| TIC SR No.: | -
MOTOR NAMEPLATE DATA
| H.P.: | 5000 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 450-1600 |  | ENCL: | WP-II |  | FLAMPS: | 603 |  |  | FLRPM: | 3587
| FORM: | DCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TKKH |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | C203WTQL11F-C |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 3720 |  |  | FULL LOAD (lb-ft.): | 7321 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 155 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 235
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 96.9 | [5 empty] | FULL LOAD: | 92.1
|  | 3/4 LOAD: | 96.7 | [5 empty] | 3/4 LOAD: | 91.2
|  | 1/2 LOAD: | 96 | [5 empty] | 1/2 LOAD: | 88
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2021-07-01
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS