## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RATFILE\DT2M35U_Rev1.rat |  |  |  |  | Date: | 2019-06-20 | Time: | 7:45
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 1750 | 3600 | DCNW | 4000 | 60 | 105 | 3579.3 / 3583.7 | 0.0058 / 0.0045 | 5811/12UDZ
Core Data |  |  | Winding Data | USA Wire Std |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.5437 | LR Test Data
Air Gap | 3.3 | [5 empty] | Rt. Slot Pitch | 30.4569 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 16 | Cross Section Area |  | Mean Value | 27.5003 | 652.1003
Core Length | 600 | 600 |  |  | UB: 304.0 | UER: 1750.0 | Eff.T.W.St. | 14.3389 | WS
OD | 670 | 368.4 | Coil Pitch | 0.62494 |  |  | Eff.T.W.Rt. | 30.0388 | 56045.5935
ID | 375 | 185 | Slot Fill | - | EBL: 50.0 | ERD1: 281.0 | St.Carter Fac. | 1.1789 | IS
Core Depth | 85 | 55.29 | Con./Slot | 18 |  | ERT: 70.00 | Rt.Carter Fac. | 1.0139 | 213.6105
Eff.Core L. | 465 | 474.3 | Wire Size 1 | (.102"x.204")x2 |  | ERH: 25.00 | Carter Factor | 1.1953 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.83141 | 32.076
Number | 48 | 38 | // Circuits | 2 |  |  | Distrib. Factor | 0.95544 | AC
Kind | Open | Trapeze | Connection | Wye |  |  | Wind. Factor | 0.79436 | 783.2956
Skew | - | 0 | MCL | 1295 | 770 |  | Reactance | (Coeff.: 0.0267)
Depth | 62.5 | 36.41 | No.Cond./Ph. | 144 |  |  |  | Running | Start
Width | 10.20 - 10.20 |  | Res. (20°C) | 0.061921 |  |  | Stator Slot | 18.5331 | 18.5331
Opening | 14.5 | 3 | (105°C) | 0.082602 | 0.06193 | 0.0068365 | Rotor Slot | 16.8041 | 14.8054
Tip Depth | 2.83 | 3 | Material | CU | CU | CU | Zigzag | 4.1275 | 3.6328
T.Min.Wid. | 10.0437 | 10.3166 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 20.8428 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 7.1922 | 6.3205
Up. R. | - | 4.72 | Weight (kg) |  |  |  | Total Resist. | 0.15137 | 0.40943
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 260.9149 | 86.2657 | 26.4494 | Total React. | 1.804 | 1.7143
Duct | 10 x 10 | 9 x 10 | Wire 2 | - | - | - | Impedance | 1.8104 | 1.7626
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 33.372 |  | Length | Section | Density | AT | Volume | Loss |  | 3578.3 | 125RPM
| Reac.= | 33.3991 | Primary Core | 52.6216 | 790.5 | 19.1745 | 1317.9308 | 72640.2367 | 7398.678 |  | 3583.7 | 100RPM
Excitation Data |  |  | Tooth | 6.25 | 1120.8738 | 13.5229 | 37.097 | 14010.9219 | 810.5182 |  | 3588.9 | 75RPM
Excit.Amps | 57.724 / 49.318 |  | Second.Core | 23.2148 | 816.966 | 18.5533 | 510.663 | Total | 8209.1962 |  | 3594.1 | 50RPM
Core Loss | 2.322 / 1.984 | Flux / Pole | Tooth | 3.641 | 929.702 | 16.3035 | 47.0291 | C.L.C. | 1.75 / 0.96 |  | 3599.2 | 25RPM
NoLoad | 57.77 / 49.36 | 15.1574 | Air Gap | 0.33 | 2488.6028 | 6.0907 | 1599.4651 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 74 / 74 |  | No Load Loss | 24005.0 / 20181.1 | W.Loss | 14366.1 / 7910.1
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 11307.2 / 21402.1 | S.Loss | 1740.0 / 958.0
Current (A) | 80.26 / 81.37 | 118.73 / 120.38 | 164.50 / 166.77 | 213.61 / 216.57 | 265.05 / 268.72 | Second. Loss | 7729.0 / 8502.1 | Total C.Loss | 16106.1 / 8868.1
Efficiency | 0.928 / 0.913 | 0.958 / 0.942 | 0.966 / 0.951 | 0.969 / 0.953 | 0.969 / 0.953 | Frict.& Wind. | 7280.0 / 10170.0 | Stray Loss | 15155.334 | 0.969 | 0.953 | 0.98349 | Eff.
P.F. | 0.633 / 0.634 | 0.828 / 0.830 | 0.889 / 0.891 | 0.9103 / 0.9128 | 0.917 / 0.919 | Starting Data |  | Slip | PF | 0.9103 | 0.9128 | 1.0027 | PF.
Slip | 0.0014 / 0.0002 | 0.0029 / 0.0016 | 0.0043 / 0.0031 | 0.0058 / 0.0045 | 0.0072 / 0.0060 | LRA | 1310.3 / 1247.8 |  |  | 213.61 | 216.57 | 1.0139 | Current
RPM | 3594.8 / 3599.2 | 3589.7 / 3594.1 | 3584.5 / 3588.9 | 3579.3 / 3583.7 | 3573.9 / 3578.3 | % | 613.4 / 584.2 |  |  | 3579.3 | 3583.7 | 1.0012 | RPM
L (Inv., MH) | 4.1897 | 4.1897 | 4.1897 | 4.1897 | 4.1897 | LRT (kg.m) | 456.4 / 262.6 |  | 0.2323
(No Load) | 4.1897 |  | Correlated to: H010286.dat |  |  | % | 128.5 / 73.9
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 4047.5136 | 0.038078 | 0.63549
IM/IW | 0.29822 | I*R1/E | 0.0075765 | Rosenberg | 485.6018 | % | 308.2 / 243.6
IW*X/E | 0.1512 | I*R2/E | 0.0057634 | Schwisky | 901.203 | Amps | 884.277 |  |  | HP0.95 | 1204.7201
SUM | 0.44942 | Friction/OP. | 0.0055764 | Tsurumi | 386.171 | Max. Output | 3896.4528 | 0.036595 | 0.649 | HP1.5 | 73207.7523
IH/I | 0.010963 | Total | 0.029879 | Thrust (1mm) | 122.5707 | % | 298.4644 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.97012 | Thrust (3 mm) | 308.1947 | Amps | 866.5519 |  |  | (RPM/1000)1.8 | 10.031
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 38 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.11539 | Coil Cur. Density |  | k | 0.0685
Depth | 36.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 69216.4656 | 4.07 / 4.13 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 37.5758 | Bar Cur. Den. |  | Load Inertia | 1003.6479
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 224450 | UB: 5.75 / 5.83 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.68741 | UER: 6.05 / 6.13 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.26622 | 0.69621 | 71.6828 | 567.6499
0.0076 | 121.7902 | 144.8072 | 0.79747 | 70.8062 | 570.5211
0.038 | 240 | 438.424 | 0.89874 | 70.2901 | 573.0349
0.088632 | 152.1803 | 516.2103 | 1 | 70 | 575.1152
0.13926 | 113.2961 | 536.6768
0.18989 | 95.6247 | 544.8555 | Acceleration Data (FV V)
0.29116 | 84.5282 | 552.1823 | Load Type: | Fan / Pump
0.39242 | 78.9033 | 556.7513 | Load Inertia: | 84.6 kg.m²
0.49368 | 75.385 | 560.7473 | Accel. Time: | 5.7 (s)
0.59495 | 73.116 | 564.39 | Rated Torque: | 355.3 kg.m
DesPro8AX Draft
Load
100
98.48
90.3
76.9558
63.7916
52.2232
34.5032
22.8337
14.5053
8.3032
6.0758
7.9495
14.9116
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | DT2M35U_Rev1 | [5 empty] | HRW / Model Number: | M353WTQL11F-C
Type: TIKE - Form: DCNW - 2 Pole - 1750 HP - 4000 V - 60 Hz - 5811/12UDZ - Class F | [11 empty] | Motor Type Selection |  | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  |  | EPACT |  | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [7 empty] | EQP-III |  | M36 - 26Ga.
Air Gap |  | 3.3 |  | No load amps |  |  |  | 49 | - |  |  | Exp.Prf. |  | NCB1 - 26Ga.
Stack length |  | 600 |  | No load watts |  |  |  | 20181 | - |  |  | Exp.Prf.-EQPIII |  | M43 - 26Ga.
Number of turns per coil |  | 9 |  | Impedance amps |  | 3 | f | 377 | - |  |  | Prem. Eff. |  | M45 - 26Ga.
Wire 1 (size & number) |  | (.102"x.204")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  |  | OWP |  | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 56046 | - |  |  | Dry Kiln
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C)
Connection |  | 2 x Wye |  |  | Winding |  | 80/115 | 74 / 98 | -
MCL |  | 1295 |  |  | Frame |  |  | - | - |  |  |  | 16.6028 | 1.118 | 1.65 | 1.8448 | 16.6028
Allowance for ins. depth |  | 9.4356 |  |  | Bearing PS/OS |  |  | - | - | [7 empty] | 8.3014
Allowance for ins. width |  | 3.7368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 18 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 217 |  | 1410.5
Coil grouping |  | - |  |  |  | RPM |  | 3585
Coil pitch (slot number) |  | 1 ~ 16 |  |  |  | CODE |  | E
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.0619 |  |  |  | DESIGN |  | - |  |  |  | Skip
Coil Weight | Wire1 | 574 |  |  |  | Nom.Eff. (%): |  | - |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 413 / 2375 | 583 / 613
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 1248 | - | 575.1% | 629%
[6 empty] | LRT (%) | 60 | 73 | -
[6 empty] | BDT (%) | 175 | 243 | -
[6 empty] | SLIP (%) |  | 0.45 | -
[5 empty] | IEEE-B | Eff. (%) |  | 95.3 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 91.3 | -
|  |  |  | Losses (Watts) |  | Primary |  | 21402 | -
[6 empty] | Secondary |  | 8502 | -
[6 empty] | Core |  | 8868 | -
[6 empty] | F & W |  | 10170 | -
[6 empty] | Stray |  | 15155 | -
End Ring (Reference) |  |  |  | Note | TOP HAT, WPII, Cu Bar, Sleeve Brg.
F&W Losses for A/F.: 5000 W
|  |  |  | LINK: | H010286.rat with H010286.dat
Run DT2M35U_Rev1.rat
361-N126-6L2Y ; 362-N126-06
TOP HAT ASSY: 135-N127-100NSS
Approved |  | Design | A. GRACIA |  | RSO2: 400-N156-01
Date |  | Date | 2003-03-24 |  | REV.1 FIRST ISSUE |  |  |  | Z.X 06/20/19
331.0
25.0
50.0
70.0
M
36.41
3.00
3.00
14.12
4.72
62.5
2.83
14.5
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on J20: Xie, Zichao: code letter might be more close to F
Note on D21: Choose Method of coil connection from list!
Note on J28: Xie, Zichao: LRA might be more close to 1365A according to H010288 LAB 2911

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 2 Pole - 1750.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 501.8 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~365 | 70.1 | 22.5 | 0.701 | 1245.7 | 270.5 | 704.8
365~729 | 70.5 | 11.4 | 0.566 | 1240.8 | 216.7 | 513.4
729~1094 | 71.2 | 7.0 | 0.521 | 1234.9 | 197.8 | 422.4
1094~1458 | 72.4 | 7.2 | 0.513 | 1228.3 | 192.8 | 367.6
1458~1823 | 74.3 | 11.4 | 0.532 | 1220.8 | 197.9 | 332.7
1823~2187 | 77.1 | 18.7 | 0.571 | 1212.5 | 209.7 | 305.5
2187~2552 | 81.7 | 28.7 | 0.631 | 1203.2 | 228.1 | 280.6
2552~2916 | 90.1 | 43.4 | 0.716 | 1190.3 | 254.7 | 253.1
2916~3099 | 104.5 | 58.0 | 0.359 | 1173.5 | 124.5 | 187.6
3099~3281 | 132.7 | 70.4 | 0.268 | 1142.4 | 90.0 | 121.4
3281~3463 | 196.1 | 83.6 | 0.149 | 1035.8 | 46.2 | 57.6
3463~3573 | 180.9 | 94.4 | 0.116 | 632.8 | 26.0 | 50.6
3573~3579 | 110.9 | 99.2 | 0.052 | 219.8 | 0.6 | 28.8
Acceleration Time: 5.7 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2056 kW / s |  | 20°C |  | 41°C
Rotor Bar Rise | 3266 kW / s |  | 98°C |  | 197°C
End Ring Rise | 360 kW / s |  | 35°C |  | 71°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 4.9°C / s |  | 494.5 kW | 160°C | 32.5 s
Rotor Bar | 24.8°C / s |  | 823.0 kW | 260°C | 10.5 s
Rotor ER | 8.9°C / s |  | 90.9 kW | 180°C | 20.2 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 98°C + |  | 62°C + | 40°C | = 200°C | 12.6 s
Rotor Bar | 138°C + |  | 122°C + | 40°C | = 300°C | 4.9 s
Rotor ER | 138°C + |  | 42°C + | 40°C | = 220°C | 4.7 s
Cold Stall Time: | 13.3 s |  | Hot Stall Time: |  | 3.1 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
CUSTOMER:
| TIC SR No.: | 2135527.1
MOTOR NAMEPLATE DATA
| H.P.: | 1750 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812USS |  | ENCL: | WP-II |  | FLAMPS: | 217 |  |  | FLRPM: | 3585
| FORM: | DCW4 |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | E |  |  | DUTY: | Cont.
| MODEL No.: | WT-10019401 |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 1248 |  |  | FULL LOAD (lb-ft.): | 2564 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 70 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 240
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.3 | [5 empty] | FULL LOAD: | 91.3
|  | 3/4 LOAD: | 95 | [5 empty] | 3/4 LOAD: | 89.1
|  | 1/2 LOAD: | 94.2 | [5 empty] | 1/2 LOAD: | 83
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2019-06-20
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | WT-10019401 |  |  | FLAmps: | 217
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 222.9 lb-ft² | Date: | 2019-06-20
FLRPM: | 3585 | Load Inertia: | 501.8 lb-ft² | File: | DT2M35U
| Locked Rotor Amps: | 1248 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 70% | Starting at: | FV (V)
| Breakdown Torque: | 240% | Accel. Time: | 5.7 (s)
| Rated Torque: | 2564 lb-ft
Comments: | PROJECT | 2135527.1 |  | D.E.Curve #: | DT2M35U
|  | Prepared by: | Zichao Xie | Checked by:
Load
100 | 0 | 0.26622 | 100
99.24 | 121.7902 | 144.8072 | 98.48
96.2 | 240 | 438.424 | 90.3
91.1368 | 152.1803 | 516.2103 | 76.9558
86.0737 | 113.2961 | 536.6768 | 63.7916
81.0105 | 95.6247 | 544.8555 | 52.2232
70.8842 | 84.5282 | 552.1823 | 34.5032
60.7579 | 78.9033 | 556.7513 | 22.8337
50.6316 | 75.385 | 560.7473 | 14.5053
40.5053 | 73.116 | 564.39 | 8.3032
30.3789 | 71.6828 | 567.6499 | 6.0758
20.2526 | 70.8062 | 570.5211 | 7.9495
10.1263 | 70.2901 | 573.0349 | 14.9116
0 | 70 | 575.1152 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | WT-10019401 |  |  | FLAmps: | 217
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 222.9 lb-ft² | Date: | 2019-06-20
FLRPM: | 3585 | Load Inertia: | 501.8 lb-ft² | File: | DT2M35U
1248 A
70%
2564 lb-ft
Comments: | PROJECT | 2135527.1 |  | D.E.Curve #: | DT2M35U
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
575.1152 | 24 | 12 |  | 575.1152 | 0.0001
525.1152 | 28.788 | 14.394 |  | 574.0553 | 0.701
475.1152 | 35.166 | 17.583 |  | 571.7972 | 1.267
425.1152 | 43.9246 | 21.9623 |  | 569.0783 | 1.788
375.1152 | 56.4146 |  |  | 566.0369 | 2.301
275.1152 | 104.8798 |  |  | 562.5806 | 2.833
240 | 137.8156 | 68.9078 |  | 558.7558 | 3.404
180 | 293.8843 | 122.5028 |  | 554.47 | 4.035
145 | 377.5591 | 188.7795 |  | 548.5253 | 4.751
125 |  | 400 |  | 540.7834 | 5.11
125 |  | 800 |  | 526.4516 | 5.378
125 |  | 10000 |  | 477.3272 | 5.527
|  |  |  | 240 | 5.643
|  |  |  | 125 | 5.695

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | WT-10019401 |  |  | FLAmps: | 217
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 222.9 lb-ft² | Date: | 2019-06-20
FLRPM: | 3585 | Load Inertia: | 501.8 lb-ft² | File: | DT2M35U
| Locked Rotor Amps: | 1248 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 70% | Starting at: | FV (V)
| Breakdown Torque: | 240% | Accel. Time: | 5.7 (s)
| Rated Torque: | 2564 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 3600 | 4000
[8 empty] | 3597 | 3600
Comments: | PROJECT | 2135527.1 |  | D.E.Curve #: | DT2M35U |  |  | 3594 | 3200
[8 empty] | 3591 | 2800
[8 empty] | 3588 | 2400
[8 empty] | 3585 | 2000
|  | Prepared by: | Zichao Xie | Checked by: |  | SYNC SPEED | 3600 | 3582 | 1600
[6 empty] | NEW SPEED LOWER RANGE | 3570 | 3579 | 1200
[6 empty] | NEW kW UPPER RANGE | 4000 | 3576 | 800
[8 empty] | 3573 | 400
[8 empty] | 3570 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 49 | 100 | 0.50453
25 | 91.3 | 63.4 | 81.37 | 87.4398 | 8.9354
50 | 94.2 | 83 | 120.38 | 75.1204 | 17.3059
75 | 95.1 | 89.1 | 166.77 | 62.5602 | 25.7369
100 | 95.3 | 91.28 | 216.57 | 50 | 34.2401
125 | 95.3 | 91.9 | 268.72 | 36.9564 | 42.7736
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 58.5733 | 100 | 24.4044
25 | 91.2561 | 63.4247 | 81.3765 | 97.7362 | 8.9393
50 | 94.2228 | 83.0475 | 120.3836 | 84.9636 | 17.3158
75 | 95.0478 | 89.135 | 166.7827 | 71.9717 | 25.7482
100 | 95.2996 | 91.279 | 216.5797 | 58.8671 | 34.2402
125 | 95.3156 | 91.9389 | 268.7363 | 45.5437 | 42.7931
3600
3597
3594
3591
3588
3585
3582
3579
3576
3573
3570
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0.0

## Circuit Param.
TOSHIBA INTERNATIONAL CORPORATION | [6 empty] | INDEX | MPCF-1109
Industrial Division / Houston Motor Plant | [6 empty] | SHEET NO. | 1 of 1
[7 empty] | ISSUED | 2004-11-18
EQUIVALENT CIRCUIT DATA | [6 empty] | SUPERSEDES | NEW
[7 empty] | REVISION | REV. 0
[7 empty] | WRITTEN BY | MDC
All Values are Presented in Ohms/Phase, Equivalent Wye Connection. | [6 empty] | APPROVED BY | Paul Anderson
| CUSTOMER: | FLOWSERVE FSG CORPORATION
| TIC SR No.: | 2135527.1
MOTOR NAMEPLATE DATA
| H.P.: | 1750 | VOLTS: | 4000 | 3 PH / | 60 Hz |  | S. RPM: | 3600
| FRAME: | 5812USS | ENCL: | WP-II | FLAMPS: | 217 |  | FLRPM: | 3585
| FORM: | DCNW | S.F.: | 1.0 | NEMA DESIGN: | - |  | INSUL CLASS: | F
| TYPE: | TIKE | AMB.: | 40°C | CODE: | E |  | DUTY: | Cont.
| MODEL No.: | WT-10019401 |  |  | kW: | -
| NOM. EFF.: | - | MIN. EFF.: | - | P.F.: | -
Primary Resistance (R1) : |  |  |  | 0.342743
Secondary Resistance (R2) : |  |  |  | 0.229565
Starting Resistance (R3) : |  |  |  | 0.776549
Primary Reactance (X1) : |  |  |  | 2.871958
Secondary Reactance (X2) : |  |  |  | 2.451798
Starting Reactance (X3) : |  |  |  | 1.8443691
Magnetizing Reactance (Xm) : |  |  |  | 127.169663
Transient Reactance : |  |  |  | 5.27738
Sub Transient Reactance : |  |  |  | 3.91567
Short Circuit Time Constant : |  |  |  | 2.4634
Sub Transient Time Constant : |  |  |  | 0.01077
Open Circuit Time Constant : |  |  |  | 1.4978
[6 empty] | CERTIFIED BY: | JERRY R
[6 empty] | DATE: | 2019-10-09

## PERFORMANCE data
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1082
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 2/14/02
[9 empty] | SUPERSEDES |  | NEW
[9 empty] | REVISION |  | 0
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | M. CAMPBELL
API 541 PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | P.A.A
| CUSTOMER: | FLOWSERVE FSG CORPORATION
| TIC SR No.: | 2135527.1
MOTOR NAMEPLATE DATA
| H.P.: | 1750 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812USS |  | ENCL: | WP-II |  | FLAMPS: | 217 |  |  | FLRPM: | 3585
| FORM: | DCNW |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | E |  |  | DUTY: | Cont.
| MODEL No.: | WT-10019401 |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
LOCKED ROTOR DATA
|  |  | AMPS AT RATED VOLTAGE: | 1248 |  |  |  | POWER FACTOR: | 21.3
|  |  | AMPS AT 80% VOLTAGE: | 998
TORQUE VALUES | [6 empty] | CURVE NUMBERS
|  |  |  | FULL LOAD (LB.FT): | 2564 |  |  |  | SPEED-TORQUE CURVE: | DT2M35U
|  |  |  | LOCKED ROTOR TORQUE (% OF FLT): | 70 |  |  |  | SPEED-CURRENT CURVE: | DT2M35U
|  |  |  | PULL UP TORQUE (% OF FLT): | 70 |  |  |  | ACCELERATION CURVE: | DT2M35U
|  |  |  | BREAKDOWN TORQUE (% OF FLT): | 240
LOCKED ROTOR WITHSTAND TIMES
COLD CONDITION | [6 empty] | HOT CONDITION
|  | 100% VOLTAGE: | 24 | [5 empty] | 100% VOLTAGE: | 12
|  | 90% VOLTAGE: | 29 | [5 empty] | 90% VOLTAGE: | 15
|  | 80% VOLTAGE: | 38 | [5 empty] | 80% VOLTAGE: | 19
|  | 70% VOLTAGE: | 49 | [5 empty] | 70% VOLTAGE: | 24
DESIGN DATA
|  | MOTOR ROTOR wk2 (LB.FT2): | 222.9 | [5 empty] | NO LOAD CURRENT: | 49
|  | AIR GAP: | 3.3 | [5 empty] | ACCELERATION TIME:
LOAD CHARACTERISTICS
|  |  | LOAD |  |  | 1/2 | 3/4 | FULL | SF
|  |  | AMPS (A) |  |  | 120 | 167 | 217 | -
|  |  | EFFICIENCY (%) |  |  | 94.2 | 95.1 | 95.3 | -
|  |  | POWER FACTOR (%) |  |  | 83 | 89.1 | 91.2 | -
|  |  | GUARENTEED EFFICIENCY (%) |  |  | - | - | - | -
EFFICIENCY TO BE DETERMINED BY IEEE 112, METHOD B
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2019-10-09
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE, FREQUENCY AND SINEWAVE POWER INPUT.