## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\BASE MV DESIGNS\6800 FRAME\Electrical Design\2P\SERIES\DT2M40UEXP_ERchange.rat |  |  |  |  | Date: | 2020-02-11 | Time: | 15:57
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 2000 | 3600 | DCNW | 4000 | 60 | 105 | 3574.7 / 3582.0 | 0.0070 / 0.0050 | 5811/12UDZ
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 24.5437 | LR Test Data
Air Gap | 3.3 | [5 empty] | Rt. Slot Pitch | 30.4569 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 17 | Cross Section Area |  | Mean Value | 27.5003 | 689.3275
Core Length | 630 | 630 |  |  | UB: 304.0 | UER: 1848.0 | Eff.T.W.St. | 14.3389 | WS
OD | 670 | 368.4 | Coil Pitch | 0.6666 |  |  | Eff.T.W.Rt. | 30.0388 | 64148.4126
ID | 375 | 185 | Slot Fill | - | EBL: 45.0 | ERD1: 284.0 | St.Carter Fac. | 1.1789 | IS
Core Depth | 85 | 55.29 | Con./Slot | 16 |  | ERT: 44.00 | Rt.Carter Fac. | 1.0139 | 242.899
Eff.Core L. | 507.78 | 513.36 | Wire Size 1 | (.114"x.204")x2 |  | ERH: 42.00 | Carter Factor | 1.1953 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.86597 | 36.0854
Number | 48 | 38 | // Circuits | 2 |  |  | Distrib. Factor | 0.95544 | AC
Kind | Open | Trapeze | Connection | Wye |  |  | Wind. Factor | 0.82738 | 791.7282
Skew | - | 0 | MCL | 1360 | 764 |  | Reactance | (Coeff.: 0.0252)
Depth | 62.5 | 36.41 | No.Cond./Ph. | 128 |  |  |  | Running | Start
Width | 10.20 - 10.20 |  | Res. (20°C) | 0.052449 |  |  | Stator Slot | 18.5331 | 18.5331
Opening | 14.5 | 3 | (105°C) | 0.069966 | 0.052671 | 0.020308 | Rotor Slot | 16.8041 | 14.8054
Tip Depth | 2.83 | 3 | Material | CU | CU | CU | Zigzag | 4.1275 | 3.6162
T.Min.Wid. | 10.0437 | 10.3166 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 20.2644 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 7.1922 | 6.2916
Up. R. | - | 4.72 | Weight (kg) |  |  |  | Total Resist. | 0.14295 | 0.36242
Wedge Dep. | 2.83 - 2.00 | Magnetic | Wire 1 | 268.4317 | 82.9794 | 33.9599 | Total React. | 1.6835 | 1.5979
Duct | 14 x 6 | 13 x 6 | Wire 2 | - | - | - | Impedance | 1.6896 | 1.6385
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 33.372 |  | Length | Section | Density | AT | Volume | Loss |  | 3575.5 | 125RPM
| Reac.= | 33.3991 | Primary Core | 52.6216 | 863.226 | 18.9656 | 1262.6244 | 79323.1383 | 7937.268 |  | 3582.0 | 100RPM
Excitation Data |  |  | Tooth | 6.25 | 1223.9941 | 13.3756 | 35.6032 | 15299.9267 | 869.5202 |  | 3588.4 | 75RPM
Excit.Amps | 61.074 / 54.550 |  | Second.Core | 23.2148 | 884.2455 | 18.5148 | 506.4527 | Total | 8806.7882 |  | 3594.8 | 50RPM
Core Loss | 2.492 / 2.226 | Flux / Pole | Tooth | 3.641 | 1006.2656 | 16.2697 | 46.6169 | C.L.C. | 1.75 / 1.04 |  | 3601.0 | 25RPM
NoLoad | 61.12 / 54.60 | 16.3716 | Air Gap | 0.33 | 2705.4316 | 6.0514 | 1589.1314 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 65 / 65 |  | No Load Loss | 25150.7 / 17700.0 | W.Loss | 15411.9 / 9180.4
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 12384.0 / 11262.0 | S.Loss | 1871.9 / 1115.1
Current (A) | 87.59 / 88.31 | 132.95 / 134.04 | 186.09 / 187.62 | 242.90 / 244.89 | 302.47 / 304.95 | Second. Loss | 10790.0 / 8317.0 | Total C.Loss | 17283.8 / 10295.5
Efficiency | 0.933 / 0.929 | 0.961 / 0.956 | 0.968 / 0.963 | 0.970 / 0.965 | 0.969 / 0.965 | Frict.& Wind. | 7280.0 / 6042.0 | Stray Loss | 17904 | 0.970 | 0.965 | 0.99485 | Eff.
P.F. | 0.659 / 0.656 | 0.843 / 0.840 | 0.897 / 0.894 | 0.914 / 0.911 | 0.918 / 0.915 | Starting Data |  | Slip | PF | 0.914 | 0.911 | 0.99672 | PF.
Slip | 0.0018 / -0.0003 | 0.0035 / 0.0015 | 0.0052 / 0.0032 | 0.0070 / 0.0050 | 0.0088 / 0.0068 | LRA | 1409.5 / 1548.5 |  |  | 242.90 | 244.89 | 1.0082 | Current
RPM | 3593.7 / 3601.0 | 3587.5 / 3594.8 | 3581.2 / 3588.4 | 3574.7 / 3582.0 | 3568.3 / 3575.5 | % | 580.3 / 637.5 |  |  | 3574.7 | 3582.0 | 1.002 | RPM
L (Inv., MH) | 3.91 | 3.91 | 3.91 | 3.91 | 3.91 | LRT (kg.m) | 472.5 / 566.9 |  | 0.22119
(No Load) | 3.91 |  | Correlated to: H402118_Test Lab 0620 & 1797_RM_LRA 3015,3016,3017.dat |  |  | % | 116.2 / 139.4
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 4358.1898 | 0.043312 | 0.63368
IM/IW | 0.27511 | I*R1/E | 0.0073234 | Rosenberg | 523.4474 | % | 290.1 / 216.2
IW*X/E | 0.16183 | I*R2/E | 0.0070152 | Schwisky | 971.4387 | Amps | 949.6764 |  |  | HP0.95 | 1367.6611
SUM | 0.43693 | Friction/OP. | 0.0048794 | Tsurumi | 414.4105 | Max. Output | 4173.6744 | 0.041406 | 0.64908 | HP1.5 | 89442.7191
IH/I | 0.010309 | Total | 0.029527 | Thrust (1mm) | 164.9839 | % | 279.7369 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.97047 | Thrust (3 mm) | 414.744 | Amps | 928.0882 |  |  | (RPM/1000)1.8 | 10.031
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 38 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.12033 | Coil Cur. Density |  | k | 0.0685
Depth | 36.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 74916.6452 | 4.20 / 4.24 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 40.6703 | Bar Cur. Den. |  | Load Inertia | 1096.1434
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 245099.4 | UB: 6.11 / 6.16 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.7499 | UER: 6.08 / 6.13 | LER: - |  | 365.3301
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.24949 | 0.68737 | 135.0039 | 623.9367
0.002 | 95.374 | 141.2515 | 0.79158 | 135.0029 | 627.1601
0.01 | 215 | 457.1487 | 0.89579 | 135.0018 | 629.9517
0.062105 | 162.9767 | 555.7051 | 1 | 135 | 632.2449
0.11421 | 144.5409 | 583.3539
0.16632 | 138.0247 | 594.7266 | Acceleration Data (FV / 0.80 V)
0.27053 | 135.2736 | 604.9908 | Load Type: | Fan / Pump
0.37474 | 135.0129 | 611.0256 | Load Inertia: | 184.8 kg.m²
0.47895 | 135.0093 | 615.9385 | Accel. Time: | 4.9 / 10.3 (s)
0.58316 | 135.0056 | 620.2142 | Rated Torque: | 406.5 kg.m
Load | Torque 80% | LRA 80%
100 | 0 | 48.8996
99.6 | 61.0394 | 113.0012
98 | 137.6 | 365.7189
83.8526 | 104.3051 | 444.5641
70.3053 | 92.5062 | 466.6832
57.4105 | 88.3358 | 475.7813
38.0105 | 86.5751 | 483.9927
24.7789 | 86.4083 | 488.8205
15.6842 | 86.4059 | 492.7508
9.0105 | 86.4036 | 496.1714
6.2526 | 86.4025 | 499.1494
7.8316 | 86.4018 | 501.7281
14.7053 | 86.4012 | 503.9614
30 | 86.4 | 505.7959

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET | [9 empty] | M401WTAL11E-CH
File: | DT2M40UEXP_ERchange | [5 empty] | HRW / Model Number: |  |  | M403WTAL11E-CH
Type: TIKE - Form: DCNW - 2 Pole - 2000 HP - 2300/4000 V - 60 Hz - 5811/12UDZ - Class F | [11 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  |  | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test 4000V 2300V | [7 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 3.3 |  | No load amps |  |  |  | 55 | 95 |  | 97 | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 630 |  | No load watts |  |  |  | 17700 | 17700 |  | 19100 | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 8 |  | Impedance amps |  | 3 | f | 405 | 423 |  | 445 | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.114"x.204")x2 |  | Impedance volts |  | 3 | f | 1150 | 460 |  |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 64148 | 64148 |  | 57903 | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [7 empty] | Dry Kiln
Connection |  | 2 Delta / 2 x Wye |  |  | Winding |  | 80/115 | 64.6 / 86 | -
MCL |  | 1360 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 10.1404 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 16 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 424 / 245 |  |  | #VALUE!
Coil grouping |  | - |  |  |  | RPM |  | 3582
Coil pitch (slot number) |  | 1 ~ 17 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.0519 |  |  |  | DESIGN |  | - |  |  |  | Skip
Coil Weight | Wire1 | 615.4 |  |  |  | Nom.Eff. (%): |  | - |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 424 / 2681 | 616 / 613
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 2683 / 1549 | - |  | #VALUE!
[6 empty] | LRT (%) | 60 | 139 | -
[6 empty] | BDT (%) | 175 | 216 | -
[6 empty] | SLIP (%) |  | 0.5 | -
[5 empty] | IEEE-B | Eff. (%) |  | 96.5 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 91.1 | -
|  |  |  | Losses (Watts) |  | Primary |  | 11262 | -
[6 empty] | Secondary |  | 8317 | -
[6 empty] | Core |  | 10296 | -
[6 empty] | F & W |  | 6042 | -
[6 empty] | Stray |  | 17904 | -
End Ring (Reference) |  |  |  | Note | DT2M40U (ER at end of bar)
|  |  |  | LINK: | DT2M40UEXP_ERchange.rat &
H402118_Test Lab 0620 & 1797_RM_LRA 3015,3016,3017.dat
361-N126-6L2DYINT (3L2YINT), 362-N126-08
RSO2: 400-H402118, 135-H402118-100
Rev.4 Remove temperature rise from 0620 test. Z.X 02/11/20
Approved |  | Design | V.Phillips |  | Rev.3 Update correlation. Z.X 07/19/2019
Date |  | Date | 2011-02-18 |  | Rev.2 Update correlation. Z.X 05/24/2019
REV5. ADDED 2300V DATA. For 2300V only,
you must use 361-N126-6L2DYINT due to FLA.
JROD 01/30/2024
284.0
42.0
45.0
44.0
36.41
3.00
3.00
14.12
4.72
62.5
2.83
14.5
311-
411-
051-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 2 Pole - 2000.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 1096.1 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~375 | 135.0 | 22.4 | 0.493 | 1546.2 | 248.1 | 959.3
375~750 | 135.0 | 11.3 | 0.448 | 1540.0 | 224.2 | 782.2
750~1125 | 135.0 | 7.0 | 0.433 | 1532.6 | 214.8 | 668.0
1125~1501 | 135.0 | 7.6 | 0.435 | 1524.1 | 213.6 | 582.8
1501~1876 | 135.0 | 12.3 | 0.452 | 1514.3 | 219.1 | 513.4
1876~2251 | 135.0 | 20.2 | 0.483 | 1503.0 | 231.0 | 450.7
2251~2626 | 135.1 | 31.4 | 0.535 | 1489.6 | 251.7 | 390.4
2626~3001 | 136.6 | 47.7 | 0.624 | 1469.7 | 287.8 | 329.4
3001~3189 | 141.3 | 63.9 | 0.358 | 1443.1 | 159.7 | 237.3
3189~3376 | 153.8 | 77.1 | 0.362 | 1395.3 | 155.1 | 172.2
3376~3564 | 189.0 | 90.9 | 0.283 | 1240.7 | 110.0 | 82.6
3564~3575 | 157.5 | 98.8 | 0.027 | 733.0 | 0.3 | 20.6
Acceleration Time: 4.9 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 2315 kW / s |  | 22°C |  | 45°C
Rotor Bar Rise | 3745 kW / s |  | 117°C |  | 234°C
End Ring Rise | 1444 kW / s |  | 110°C |  | 221°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 5.6°C / s |  | 580.5 kW | 160°C | 28.5 s
Rotor Bar | 45.5°C / s |  | 1453.7 kW | 260°C | 5.7 s
Rotor ER | 42.9°C / s |  | 560.5 kW | 180°C | 4.2 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 65°C + |  | 95°C + | 40°C | = 200°C | 17.0 s
Rotor Bar | 85°C + |  | 175°C + | 40°C | = 300°C | 3.8 s
Rotor ER | 85°C + |  | 95°C + | 40°C | = 220°C | 2.2 s
Cold Stall Time: | 10.0 s |  | Hot Stall Time: |  | 5.3 s

## Performance Data Sheet 2000HP
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | HEARTLAND MOTORS INC
| TIC SR No.: | 2374928.4
MOTOR NAMEPLATE DATA
| H.P.: | 2000 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812USS |  | ENCL: | WP-II |  | FLAMPS: | 245 |  |  | FLRPM: | 3582
| FORM: | DCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | M401WTAL11E-CH |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 1549 |  |  | FULL LOAD (lb-ft.): | 2932 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 135 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 215
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 96.5 | [5 empty] | FULL LOAD: | 91.1
|  | 3/4 LOAD: | 96.3 | [5 empty] | 3/4 LOAD: | 89.4
|  | 1/2 LOAD: | 95.6 | [5 empty] | 1/2 LOAD: | 84
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2024-01-30
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve 2000HP
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | M401WTAL11E-CH |  |  | FLAmps: | 245
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2000 | Rotor Inertia: | 241.3 lb-ft² | Date: | 2024-01-30
FLRPM: | 3582 | Load Inertia: | 365.0 lb-ft² | File: | DT2M40U
| Locked Rotor Amps: | 1549 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 135% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 215% | Accel. Time: | 2 / 4 (s)
| Rated Torque: | 2932 lb-ft
Comments: | PROJECT | 2374928.4 |  | D.E.Curve #: | DT2M40U
|  | Prepared by: | JERRY R | Checked by:
|  |  | Load | Torque 80% | LRA 80%
100 | 0 | 0.24949 | 100 | 0 | 48.8996
99.8 | 95.374 | 141.2515 | 99.6 | 61.0394 | 113.0012
99 | 215 | 457.1487 | 98 | 137.6 | 365.7189
93.7895 | 162.9767 | 555.7051 | 83.8526 | 104.3051 | 444.5641
88.5789 | 144.5409 | 583.3539 | 70.3053 | 92.5062 | 466.6832
83.3684 | 138.0247 | 594.7266 | 57.4105 | 88.3358 | 475.7813
72.9474 | 135.2736 | 604.9908 | 38.0105 | 86.5751 | 483.9927
62.5263 | 135.0129 | 611.0256 | 24.7789 | 86.4083 | 488.8205
52.1053 | 135.0093 | 615.9385 | 15.6842 | 86.4059 | 492.7508
41.6842 | 135.0056 | 620.2142 | 9.0105 | 86.4036 | 496.1714
31.2632 | 135.0039 | 623.9367 | 6.2526 | 86.4025 | 499.1494
20.8421 | 135.0029 | 627.1601 | 7.8316 | 86.4018 | 501.7281
10.4211 | 135.0018 | 629.9517 | 14.7053 | 86.4012 | 503.9614
0 | 135 | 632.2449 | 30 | 86.4 | 505.7959

## Thermdam 2000HP
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | M401WTAL11E-CH |  |  | FLAmps: | 245
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2000 | Rotor Inertia: | 241.3 lb-ft² | Date: | 2024-01-30
FLRPM: | 3582 | Load Inertia: | 365.0 lb-ft² | File: | DT2M40U
1549 A
135%
2932 lb-ft
Comments: | PROJECT | 2374928.4 |  | D.E.Curve #: | DT2M40U
|  | Prepared by: | JERRY R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
632.2449 | 14.2357 | 7.4287 |  | 632.2449 | 0.0001 | 505.7959 | 0.0001
600 | 15.8069 | 8.2486 |  | 631.102 | 0.19063 | 504.8816 | 0.38065
500 | 22.7619 | 11.878 |  | 628.6939 | 0.3625 | 502.9551 | 0.72387
400 | 35.5655 | 18.5593 |  | 625.9592 | 0.52969 | 500.7673 | 1.0577
300 | 63.2275 |  |  | 622.8163 | 0.69688 | 498.2531 | 1.3916
200 | 142.2619 |  |  | 619.3061 | 0.86875 | 495.4449 | 1.7348
215 | 123.1038 | 64.2399 |  | 615.3878 | 1.0516 | 492.3102 | 2.0998
180 | 195.0166 | 91.6509 |  | 611.0612 | 1.2562 | 488.849 | 2.5086
145 | 270.6528 | 141.2361 |  | 605.2245 | 1.4922 | 484.1796 | 2.9797
125 |  | 300 |  | 597.8367 | 1.6266 | 478.2694 | 3.248
125 |  | 600 |  | 584.3673 | 1.7609 | 467.4939 | 3.5164
125 |  | 10000 |  | 536.8571 | 1.8656 | 429.4857 | 3.7254
|  |  |  | 336.2449 | 1.9578 | 268.9959 | 3.9095
|  |  |  | 120 | 2.0031 | 120 | 4

## Performance 4000V 2000HP
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | M401WTAL11E-CH |  |  | FLAmps: | 245 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2000 | Rotor Inertia: | 241.3 lb-ft² | Date: | 2024-01-30
FLRPM: | 3582 | Load Inertia: | 365.0 lb-ft² | File: | DT2M40U
| Locked Rotor Amps: | 1549 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 135% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 215% | Accel. Time: | 2 / 4 (s)
| Rated Torque: | 2932 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 3600 | 4000
[8 empty] | 3596 | 3600
Comments: | PROJECT | 2374928.4 |  | D.E.Curve #: | DT2M40U |  |  | 3592 | 3200
[8 empty] | 3588 | 2800
[8 empty] | 3584 | 2400
[8 empty] | 3580 | 2000
|  | Prepared by: | JERRY R | Checked by: |  | SYNC SPEED | 3600 | 3576 | 1600
[6 empty] | NEW SPEED LOWER RANGE | 3560 | 3572 | 1200
[6 empty] | NEW kW UPPER RANGE | 4000 | 3568 | 800
[8 empty] | 3564 | 400
[8 empty] | 3560 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 55 | 100 | 0.4425
25 | 92.9 | 65.6 | 88.31 | 88.7962 | 10.034
50 | 95.6 | 84 | 134.04 | 77.7636 | 19.5018
75 | 96.3 | 89.4 | 187.62 | 66.5609 | 29.0521
100 | 96.5 | 91.1 | 244.89 | 55 | 38.6412
125 | 96.5 | 91.5 | 304.95 | 43.6173 | 48.3293
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 61.6258 | 100 | 25.2733
25 | 92.8194 | 65.655 | 88.3103 | 84.2213 | 10.0422
50 | 95.5559 | 84.0369 | 134.0357 | 68.7323 | 19.5091
75 | 96.2718 | 89.3852 | 187.6182 | 52.9412 | 29.0461
100 | 96.4529 | 91.1361 | 244.8907 | 36.8635 | 38.6554
125 | 96.4145 | 91.5208 | 304.9482 | 20.7331 | 48.3386
3600
3596
3592
3588
3584
3580
3576
3572
3568
3564
3560
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance 2300V 2000HP
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | M401WTAL11E-CH |  |  | FLAmps: | 424 A
Enclosure: | WP-II | Voltage: | 2300 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 2000 | Rotor Inertia: | 241.3 lb-ft² | Date: | 2024-01-30
FLRPM: | 3582 | Load Inertia: | 365.0 lb-ft² | File: | DT2M40U
| Locked Rotor Amps: | 2683 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 135% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 215% | Accel. Time: | 2 / 4 (s)
| Rated Torque: | 2932 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 3600 | 4000
[8 empty] | 3596 | 3600
Comments: | PROJECT | 2374928.4 |  | D.E.Curve #: | DT2M40U |  |  | 3592 | 3200
[8 empty] | 3588 | 2800
[8 empty] | 3584 | 2400
[8 empty] | 3580 | 2000
|  | Prepared by: | JERRY R | Checked by: |  | SYNC SPEED | 3600 | 3576 | 1600
[6 empty] | NEW SPEED LOWER RANGE | 3560 | 3572 | 1200
[6 empty] | NEW kW UPPER RANGE | 4000 | 3568 | 800
[8 empty] | 3564 | 400
[8 empty] | 3560 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 95.2628 | 100 | 0.4425
25 | 92.9 | 65.6 | 152.9574 | 88.7962 | 10.034
50 | 95.6 | 84 | 232.1641 | 77.7636 | 19.5018
75 | 96.3 | 89.4 | 324.9674 | 66.5609 | 29.0521
100 | 96.5 | 91.1 | 424 | 55 | 38.6412
125 | 96.5 | 91.5 | 528.1889 | 43.6173 | 48.3293
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 61.6258 | 100 | 25.2733
25 | 92.8194 | 65.655 | 88.3103 | 84.2213 | 10.0422
50 | 95.5559 | 84.0369 | 134.0357 | 68.7323 | 19.5091
75 | 96.2718 | 89.3852 | 187.6182 | 52.9412 | 29.0461
100 | 96.4529 | 91.1361 | 244.8907 | 36.8635 | 38.6554
125 | 96.4145 | 91.5208 | 304.9482 | 20.7331 | 48.3386
3600
3596
3592
3588
3584
3580
3576
3572
3568
3564
3560
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0

## Circuit Param
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | INDEX | MPCF-1109
Industrial Division / Houston Motor Plant | [7 empty] | SHEET NO. | 1 of 1
[8 empty] | ISSUED | 2004-11-18
EQUIVALENT CIRCUIT DATA | [7 empty] | SUPERSEDES | NEW
[8 empty] | REVISION | REV. 0
[8 empty] | WRITTEN BY | MDC
All Values are Presented in Ohms/Phase, Equivalent Wye Connection. | [7 empty] | APPROVED BY | Paul Anderson
| CUSTOMER: | JOHNSON CONTROL INC
| TIC SR No.: | 2177141.1
MOTOR NAMEPLATE DATA
| H.P.: | 2000 | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  | S. RPM: | 3600
| FRAME: | 5812UDZ | ENCL: | WP-II |  | FLAMPS: | 245 |  | FLRPM: | 3582
| FORM: | DCNLW | S.F.: | 1.0 |  | NEMA DESIGN: | - |  | INSUL CLASS: | F
| TYPE: | TIKE | AMB.: | 40°C |  | CODE: | F |  | DUTY: | Cont.
| MODEL No.: | A1-10032592 |  |  |  | kW: | -
| NOM. EFF.: | 96.2 | MIN. EFF.: | - |  | P.F.: | 91
Primary Resistance (R1) : |  |  |  |  | 0.0699
Secondary Resistance (R2) : |  |  |  |  | 0.0729
Starting Secondary Resistance (R3) : |  |  |  |  | 0.0292
Primary Reactance (X1) : |  |  |  |  | 1.031
Secondary Reactance (X2) : |  |  |  |  | 1.015
Starting Secondary Reactance (X3) : |  |  |  |  | 0.652
Magnetizing Reactance (Xm) : |  |  |  |  | 41.9
Transient Reactance : |  |  |  |  | 2.3
Sub Transient Reactance : |  |  |  |  | 1.7
Short Circuit Time Constant : |  |  |  |  | 1.051
Sub Transient Time Constant : |  |  |  |  | 0.011
Open Circuit Time Constant : |  |  |  |  | 1.56
[7 empty] | CERTIFIED BY: | JERRY R
[7 empty] | DATE: | 2020-05-26

## Performance API
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1082
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 2/14/02
[9 empty] | SUPERSEDES |  | NEW
[9 empty] | REVISION |  | 0
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | M. CAMPBELL
API 541 PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | P.A.A
| CUSTOMER: | JOHNSON CONTROL INC
| TIC SR No.: | 2177141.1
MOTOR NAMEPLATE DATA
| H.P.: | 2000 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812UDZ |  | ENCL: | WP-II |  | FLAMPS: | 245 |  |  | FLRPM: | 3582
| FORM: | DCNLW |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10032592 |  |  |  |  | kW: | -
| NOM. EFF.: | 96.2 |  | MIN. EFF.: | - |  | P.F.: | 91
LOCKED ROTOR DATA
|  |  | AMPS AT RATED VOLTAGE: | 1545 A |  |  |  | POWER FACTOR: | 22.3%
|  |  | AMPS AT 80% VOLTAGE: | 1226 A
TORQUE VALUES | [6 empty] | CURVE NUMBERS
|  |  |  | FULL LOAD (LB.FT): | 1549 |  |  |  | SPEED-TORQUE CURVE: | DT2M40U_REV4.
|  |  |  | LOCKED ROTOR TORQUE (% OF FLT): | 135 |  |  |  | SPEED-CURRENT CURVE: | DT2M40U_REV4.
|  |  |  | PULL UP TORQUE (% OF FLT): | 135 |  |  |  | ACCELERATION CURVE: | DT2M40U_REV4.
|  |  |  | BREAKDOWN TORQUE (% OF FLT): | 215
LOCKED ROTOR WITHSTAND TIMES
COLD CONDITION | [6 empty] | HOT CONDITION
|  | 100% VOLTAGE: | 14 (s) | [5 empty] | 100% VOLTAGE: | 8 (s)
|  | 90% VOLTAGE: | 17 (s) | [5 empty] | 90% VOLTAGE: | 10 (s)
|  | 80% VOLTAGE: | 22 (s) | [5 empty] | 80% VOLTAGE: | 13 (s)
|  | 70% VOLTAGE: | 28 (s) | [5 empty] | 70% VOLTAGE: | 16 (s)
DESIGN DATA
|  | MOTOR ROTOR wk2 (LB.FT2): | 241.3 | [5 empty] | NO LOAD CURRENT: | 56 A
|  | AIR GAP: | 3.3 mm | [5 empty] | ACCELERATION TIME: | 2 / 3 (s)
LOAD CHARACTERISTICS
|  |  | LOAD |  |  | 1/2 | 3/4 | FULL | SF
|  |  | AMPS (A) |  |  | 134 | 188 | 245 | -
|  |  | EFFICIENCY (%) |  |  | 95.6 | 96.3 | 96.5 | -
|  |  | POWER FACTOR (%) |  |  | 84 | 89.4 | 91.1 | -
|  |  | GUARENTEED EFFICIENCY (%) |  |  | - | - | - | -
EFFICIENCY TO BE DETERMINED BY IEEE 112, METHOD B
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2020-05-26
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE, FREQUENCY AND SINEWAVE POWER INPUT.

## Performance Data Sheet 1750HP
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | HEARTLAND MOTORS INC
| TIC SR No.: | 2374928.4
MOTOR NAMEPLATE DATA
| H.P.: | 1750 |  | VOLTS: | 2300/4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 5812USS |  | ENCL: | WP-II |  | FLAMPS: | 372/215 |  |  | FLRPM: | 3585
| FORM: | DCKW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40 |  | CODE: | G |  |  | DUTY: | Cont.
| MODEL No.: | 3UKM40L1S50150 |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 2683/1549 |  |  | FULL LOAD (lb-ft.): | 2564 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 155 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 245
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 96.7 | [5 empty] | FULL LOAD: | 90.5
|  | 3/4 LOAD: | 96.4 | [5 empty] | 3/4 LOAD: | 88
|  | 1/2 LOAD: | 95.5 | [5 empty] | 1/2 LOAD: | 81.4
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Jerry R
[9 empty] | DATE: | 2025-08-28
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve 1750HP
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | 3UKM40L1S50150 |  |  | FLAmps: | 372/215 A
Enclosure: | WP-II | Voltage: | 2300/4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 241.3 lb-ft² | Date: | 2025-08-28
FLRPM: | 3585 | Load Inertia: | 335.4 lb-ft² | File: | H110345
| Locked Rotor Amps: | 2683/1549 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 155% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 245% | Accel. Time: | 2 / 4 (s)
| Rated Torque: | 2564 lb-ft
Comments: | PROJECT | 2374928.4 |  | D.E.Curve #: | H110345
|  | Prepared by: | Jerry R | Checked by:
|  |  | Load | Torque 80% | LRA 80%
100 | 0 | 0.2843 | 100 | 0 | 48.8996
99.2 | 108.682 | 160.961 | 98.4 | 69.5565 | 128.7688
96 | 245 | 520.9368 | 89.75 | 156.8 | 416.7495
90.8571 | 196.8911 | 633.2454 | 76.2286 | 126.0103 | 506.5963
85.7143 | 169.1042 | 664.7522 | 62.8571 | 108.2267 | 531.8018
80.5714 | 159.3508 | 677.7118 | 51.2571 | 101.9845 | 542.1694
70.2857 | 155.3094 | 689.4081 | 33.4857 | 99.398 | 551.5266
60 | 155 | 696.285 | 22 | 99.2 | 557.028
50 | 155 | 701.8834 | 14 | 99.2 | 561.5067
40 | 155.0018 | 706.7558 | 8 | 99.2012 | 565.4047
30 | 155.0025 | 710.9976 | 6 | 99.2016 | 568.7981
20 | 155.0058 | 714.6708 | 8 | 99.2037 | 571.7367
10 | 155.0083 | 717.852 | 15 | 99.2053 | 574.2816
0 | 155 | 720.4651 | 30 | 99.2 | 576.3721

## Thermdam 1750HP
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | 3UKM40L1S50150 |  |  | FLAmps: | 372/215 A
Enclosure: | WP-II | Voltage: | 2300/4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 241.3 lb-ft² | Date: | 2025-08-28
FLRPM: | 3585 | Load Inertia: | 335.4 lb-ft² | File: | H110345
Comments: | PROJECT | 2374928.4 |  | D.E.Curve #: | H110345
|  | Prepared by: | Jerry R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
720.4651 | 14.3189 | 9.2554 |  | 720.4651 | 0.0001 | 576.3721 | 0.0001
700 | 15.1684 | 9.8045 |  | 719.1628 | 0.198 | 575.3302 | 0.396
600 | 20.6459 | 13.345 |  | 716.2791 | 0.381 | 573.0233 | 0.762
500 | 29.73 | 19.2168 |  | 712.8372 | 0.558 | 570.2698 | 1.116
400 | 46.4532 |  |  | 708.8837 | 0.735 | 567.107 | 1.47
300 | 82.5834 |  |  | 704.3256 | 0.917 | 563.4605 | 1.834
245 | 123.8236 | 80.0365 |  | 699.0698 | 1.109 | 559.2558 | 2.218
180 | 243.0078 | 148.2774 |  | 692.8372 | 1.321 | 554.2698 | 2.642
145 | 353.5082 | 228.4988 |  | 683.5814 | 1.556 | 546.8651 | 3.112
125 |  | 500 |  | 671.2093 | 1.682 | 536.9674 | 3.364
125 |  | 1000 |  | 648.9767 | 1.801 | 519.1814 | 3.602
125 |  | 10000 |  | 577.0698 | 1.899 | 461.6558 | 3.798
|  |  |  | 340.9302 | 2 | 272.7442 | 4
|  |  |  | 120 | 2 | 120 | 4 | 0.95238

## Performance 4000V 1750HP
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 3UKM40L1S50150 |  |  | FLAmps: | 215 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 241.3 lb-ft² | Date: | 2025-08-28
FLRPM: | 3585 | Load Inertia: | 335.4 lb-ft² | File: | H110345
| Locked Rotor Amps: | 1549 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 155% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 245% | Accel. Time: | 2 / 4 (s)
| Rated Torque: | 2564 lb-ft
Comments: | PROJECT | 2374928.4 |  | D.E.Curve #: | H110345
|  | Prepared by: | Jerry R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 61.3691 | 100 | 0.4425
25 | 92.3559 | 68.734 | 74.1016 | 100.9045 | 8.8216
50 | 95.4851 | 81.4013 | 121.0396 | 87.4367 | 17.065
75 | 96.3956 | 88.0273 | 166.3072 | 69.1152 | 25.3557
100 | 96.7018 | 90.5034 | 214.9934 | 50.4965 | 33.7006
125 | 96.7591 | 91.3803 | 266.0051 | 31.8937 | 42.1008
3600
3597
3594
3591
3588
3585
3582
3579
3576
3573
3570
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0

## Performance 2300V 1750HP
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | 3UKM40L1S50150 |  |  | FLAmps: | 372 A
Enclosure: | WP-II | Voltage: | 2300 V | Frame: | 5812USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1750 | Rotor Inertia: | 241.3 lb-ft² | Date: | 2025-08-28
FLRPM: | 3585 | Load Inertia: | 335.4 lb-ft² | File: | H110345
| Locked Rotor Amps: | 2683 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 155% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 245% | Accel. Time: | 2 / 4 (s)
| Rated Torque: | 2564 lb-ft
Comments: | PROJECT | 2374928.4 |  | D.E.Curve #: | H110345
|  | Prepared by: | Jerry R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 61.3691 | 100 | 0.4425
25 | 92.3559 | 68.734 | 74.1016 | 100.9045 | 8.8216
50 | 95.4851 | 81.4013 | 121.0396 | 87.4367 | 17.065
75 | 96.3956 | 88.0273 | 166.3072 | 69.1152 | 25.3557
100 | 96.7018 | 90.5034 | 214.9934 | 50.4965 | 33.7006
125 | 96.7591 | 91.3803 | 266.0051 | 31.8937 | 42.1008
3600
3597
3594
3591
3588
3585
3582
3579
3576
3573
3570
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0