## DesignSheet 0.8V
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RAT FILES\DT2M80U.rat |  |  |  |  | Date: | 2025-07-15 | Time: | 6:28
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 4000 | 3600 | DCW | 3200 | 60 | 105 | 3565.9 / 3576.7 | 0.0095 / 0.0065 | 6813USS
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 26.1799 | LR Test Data
Air Gap | 3.5 | [5 empty] | Rt. Slot Pitch | 30.2549 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 18 | Cross Section Area |  | Mean Value | 28.2174 | 800.7802
Core Length | 820 | 820 |  |  | UB: 322.1 | UER: 3768.4 | Eff.T.W.St. | 17.1276 | WS
OD | 815 | 443 | Coil Pitch | 0.62957 |  |  | Eff.T.W.Rt. | 29.8593 | 175493.9894
ID | 450 | 170 | Slot Fill | - | EBL: 62.5 | ERD1: 328.0 | St.Carter Fac. | 1.5285 | IS
Core Depth | 109.5 | 98.09 | Con./Slot | 10 |  | ERT: 65.54 | Rt.Carter Fac. | 1.0132 | 592.5699
Eff.Core L. | 617.52 | 673.32 | Wire Size 1 | (.081"x.258")x2 |  | ERH: 57.50 | Carter Factor | 1.5488 | Volts / Turn
Slot Data |  |  | Wire Size 2 | (.081"x.258")x2 |  |  | Short. Factor | 0.83543 | 41.0572
Number | 54 | 46 | // Circuits | 2 |  |  | Distrib. Factor | 0.95529 | AC
Kind | Open | Trapeze | Connection | Wye |  |  | Wind. Factor | 0.79808 | 1131.7261
Skew | - | 0 | MCL | 1687 | 1010.537 |  | Reactance | (Coeff.: 0.0124)
Depth | 73 | 38.41 | No.Cond./Ph. | 90 |  |  |  | Running | Start
Width | 17.30 - 17.30 |  | Res. (20°C) | 0.025097 |  |  | Stator Slot | 14.9933 | 14.9933
Opening | 17.3 | 3 | (105°C) | 0.033478 | 0.025016 | 0.0055189 | Rotor Slot | 16.3182 | 13.7978
Tip Depth | 13.15 | 3 | Material | CU | CU | CU | Zigzag | 4.6908 | 4.2423
T.Min.Wid. | 8.8799 | 10.8884 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 22.0623 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 6.7858 | 6.1452
Up. R. | - | 5.72 | Weight (kg) |  |  |  | Total Resist. | 0.064013 | 0.16659
Wedge Dep. | 0.80 - 2.40 | Normal | Wire 1 | 213.3746 | 141.7576 | 84.5315 | Total React. | 0.80728 | 0.76224
Duct | 26 x 6 | 16 x 6 | Wire 2 | 213.3746 | - | - | Impedance | 0.80981 | 0.78024
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.3592 |  | Length | Section | Density | AT | Volume | Loss |  | 3567.6 | 125RPM |  | Kline/in2
| Reac.= | 35.3955 | Primary Core | 64.0099 | 1352.3688 | 14.2795 | 471.785 | 149868.957 | 9469.1119 |  | 3576.7 | 100RPM |  | 92.1254
Excitation Data |  |  | Tooth | 7.3 | 1480.5522 | 13.0432 | 38.0006 | 21616.0619 | 1179.402 |  | 3585.7 | 75RPM |  | 84.1494
Excit.Amps | 60.774 / 58.495 |  | Second.Core | 28.7597 | 1702.4672 | 11.343 | 100.2682 | Total | 10648.5139 |  | 3594.5 | 50RPM |  | 73.1806
Core Loss | 4.499 / 4.330 | Flux / Pole | Tooth | 3.841 | 1686.2202 | 11.4523 | 13.769 | C.L.C. | 1.75 / 0.86 |  | 3602.6 | 25RPM |  | 73.8857
NoLoad | 60.94 / 58.65 | 19.3111 | Air Gap | 0.35 | 3167.4043 | 6.0968 | 1698.0963 | S.F.C. | 6.05 |  |  |  |  | 39.3343
Load Characteristics |  |  | Temp. Rise @ 100%: | 79 / 73 |  | No Load Loss | 35939.1 / 40319.0 | W.Loss | 18634.9 / 9150.0
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 35266.8 / 33377.5 | S.Loss | 6326.1 / 3106.2
Current (A) | 158.75 / 166.34 | 294.40 / 308.47 | 439.04 / 460.03 | 592.57 / 620.90 | 757.09 / 793.29 | Second. Loss | 30042.4 / 15912.4 | Total C.Loss | 24961.0 / 12256.1
Efficiency | 0.949 / 0.935 | 0.967 / 0.953 | 0.970 / 0.956 | 0.968 / 0.954 | 0.965 / 0.951 | Frict.& Wind. | 10700.0 / 29487.0 | Stray Loss | 52673.0859 | 0.968 | 0.954 | 0.98554 | Eff.
P.F. | 0.893 / 0.865 | 0.946 / 0.916 | 0.949 / 0.919 | 0.938 / 0.909 | 0.921 / 0.892 | Starting Data |  | Slip | PF | 0.938 | 0.909 | 0.96908 | PF.
Slip | 0.0023 / -0.0007 | 0.0045 / 0.0015 | 0.0070 / 0.0040 | 0.0095 / 0.0065 | 0.0120 / 0.0090 | LRA | 2368.0 / 2451.1 |  |  | 592.57 | 620.90 | 1.0478 | Current
RPM | 3591.8 / 3602.6 | 3583.7 / 3594.5 | 3575.0 / 3585.7 | 3565.9 / 3576.7 | 3556.9 / 3567.6 | % | 399.6 / 413.6 |  |  | 3565.9 | 3576.7 | 1.003 | RPM
L (Inv., MH) | 1.8171 | 1.8171 | 1.8171 | 1.8171 | 1.8142 | LRT (kg.m) | 607.1 / 663.8 |  | 0.21353
(No Load) | 1.8171 |  | Correlated to: lab 1925 2420.dat |  |  | % | 74.5 / 81.4
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 5924.5948 | 0.037792 | 0.64912
IM/IW | 0.10612 | I*R1/E | 0.010798 | Rosenberg | 775.4013 | % | 196.7 / 140.8
IW*X/E | 0.25022 | I*R2/E | 0.0094646 | Schwisky | 1110.625 | Amps | 1584.4409 |  |  | HP0.95 | 2642.1471
SUM | 0.35635 | Friction/OP. | 0.0035858 | Tsurumi | 380.0958 | Max. Output | 5705.0902 | 0.036336 | 0.66276 | HP1.5 | 252982.2128
IH/I | 0.0075495 | Total | 0.031398 | Thrust (1mm) | 280.0463 | % | 191.1893 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.9686 | Thrust (3 mm) | 714.472 | Amps | 1553.0448 |  |  | (RPM/1000)1.8 | 10.031
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 46 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.20939 | Coil Cur. Density |  | k | 0.0685
Depth | 38.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 142084.276 | 5.62 / 5.89 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 111.5356 | Bar Cur. Den. |  | Load Inertia | 1570.0039
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 441045.4 | UB: 8.33 / 8.73 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.69435 | UER: 5.22 / 5.47 | LER: -
S-T Curve Data
Slip | Torque (%) | Amps | Slip | Torque (%) | Amps
0 | 0 | 0 | 0.7 | 85.201 | 2394.001
0.01 | 103.5689 | 604.8374 | 0.8 | 81.3691 | 2407.3701
0.05 | 202.1729 | 1834.4198 | 0.9 | 77.9941 | 2418.7756
0.1 | 155.5532 | 2154.0879 | 1 | 75.023 | 2428.6125
0.15 | 129.6164 | 2239.1064
0.2 | 117.0517 | 2275.1448
0.3 | 105.8434 | 2312.219
0.4 | 99.5725 | 2337.9048
0.5 | 94.3082 | 2359.6299
0.6 | 89.5183 | 2378.2253

## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RAT FILES\DT2M80U.rat |  |  |  |  | Date: | 2025-07-15 | Time: | 5:46
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
2 | 4000 | 3600 | DCW | 4000 | 60 | 105 | 3578.9 / 3589.7 | 0.0059 / 0.0029 | 6813USS
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 26.1799 | LR Test Data
Air Gap | 3.5 | [5 empty] | Rt. Slot Pitch | 30.2549 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 18 | Cross Section Area |  | Mean Value | 28.2174 | 629.3815
Core Length | 820 | 820 |  |  | UB: 322.1 | UER: 3768.4 | Eff.T.W.St. | 17.1276 | WS
OD | 815 | 443 | Coil Pitch | 0.62957 |  |  | Eff.T.W.Rt. | 29.8593 | 112057.1071
ID | 450 | 170 | Slot Fill | - | EBL: 62.5 | ERD1: 328.0 | St.Carter Fac. | 1.5285 | IS
Core Depth | 109.5 | 98.09 | Con./Slot | 10 |  | ERT: 65.54 | Rt.Carter Fac. | 1.0132 | 473.5089
Eff.Core L. | 617.52 | 673.32 | Wire Size 1 | (.081"x.258")x2 |  | ERH: 57.50 | Carter Factor | 1.5488 | Volts / Turn
Slot Data |  |  | Wire Size 2 | (.081"x.258")x2 |  |  | Short. Factor | 0.83543 | 51.3215
Number | 54 | 46 | // Circuits | 2 |  |  | Distrib. Factor | 0.95529 | AC
Kind | Open | Trapeze | Connection | Wye |  |  | Wind. Factor | 0.79808 | 904.3362
Skew | - | 0 | MCL | 1687 | 1010.537 |  | Reactance | (Coeff.: 0.0124)
Depth | 73 | 38.41 | No.Cond./Ph. | 90 |  |  |  | Running | Start
Width | 17.30 - 17.30 |  | Res. (20°C) | 0.025097 |  |  | Stator Slot | 14.9933 | 14.9933
Opening | 17.3 | 3 | (105°C) | 0.033478 | 0.025016 | 0.0055189 | Rotor Slot | 16.3182 | 13.7978
Tip Depth | 13.15 | 3 | Material | CU | CU | CU | Zigzag | 4.6908 | 3.8117
T.Min.Wid. | 8.8799 | 10.8884 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 22.0623 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 6.7858 | 5.5342
Up. R. | - | 5.72 | Weight (kg) |  |  |  | Total Resist. | 0.064013 | 0.16659
Wedge Dep. | 0.80 - 2.40 | Normal | Wire 1 | 213.3746 | 141.7576 | 84.5315 | Total React. | 0.80728 | 0.74913
Duct | 26 x 6 | 16 x 6 | Wire 2 | 213.3746 | - | - | Impedance | 0.80981 | 0.76743
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 35.3592 |  | Length | Section | Density | AT | Volume | Loss |  | 3584.4 | 125RPM |  | Kline/in2
| Reac.= | 35.3955 | Primary Core | 64.0099 | 1352.3688 | 17.8493 | 1205.0332 | 149868.957 | 13592.6283 |  | 3589.7 | 100RPM |  | 115.1568
Excitation Data |  |  | Tooth | 7.3 | 1480.5522 | 16.304 | 94.3012 | 21616.0619 | 1692.9965 |  | 3595.1 | 75RPM |  | 105.1867
Excit.Amps | 95.704 / 92.115 |  | Second.Core | 28.7597 | 1702.4672 | 14.1788 | 205.9041 | Total | 15285.6248 |  | 3600.4 | 50RPM |  | 91.4757
Core Loss | 5.381 / 5.179 | Flux / Pole | Tooth | 3.841 | 1686.2202 | 14.3154 | 28.6049 | C.L.C. | 1.75 / 0.86 |  | 3605.6 | 25RPM |  | 92.3571
NoLoad | 95.85 / 92.26 | 24.1389 | Air Gap | 0.35 | 3167.4043 | 7.621 | 2122.6203 | S.F.C. | 6.05 |  |  |  |  | 49.1678
Load Characteristics |  |  | Temp. Rise @ 100%: | 49 / 52 |  | No Load Loss | 48708.3 / 54644.4 | W.Loss | 26749.8 / 13134.5
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 22518.7 / 21312.3 | S.Loss | 10568.9 / 5189.4
Current (A) | 155.48 / 161.74 | 251.73 / 261.86 | 359.92 / 374.41 | 473.51 / 492.57 | 591.55 / 615.37 | Second. Loss | 17951.1 / 9508.1 | Total C.Loss | 37318.7 / 18323.9
Efficiency | 0.935 / 0.929 | 0.962 / 0.955 | 0.969 / 0.962 | 0.972 / 0.964 | 0.971 / 0.964 | Frict.& Wind. | 10700.0 / 29487.0 | Stray Loss | 31473.5566 | 0.972 | 0.964 | 0.99177 | Eff.
P.F. | 0.740 / 0.717 | 0.889 / 0.861 | 0.926 / 0.896 | 0.936 / 0.907 | 0.937 / 0.907 | Starting Data |  | Slip | PF | 0.936 | 0.907 | 0.96902 | PF.
Slip | 0.0015 / -0.0016 | 0.0029 / -0.0001 | 0.0044 / 0.0014 | 0.0059 / 0.0029 | 0.0073 / 0.0043 | LRA | 3009.4 / 3115.0 |  |  | 473.51 | 493 | 1.0412 | Current
RPM | 3594.8 / 3605.6 | 3589.6 / 3600.4 | 3584.3 / 3595.1 | 3578.9 / 3589.7 | 3573.6 / 3584.4 | % | 635.5 / 657.9 |  |  | 3578.9 | 3589 | 1.0028 | RPM
L (Inv., MH) | 1.8171 | 1.8171 | 1.8171 | 1.8171 | 1.8171 | LRT (kg.m) | 980.5 / 1072.1 |  | 0.21709
(No Load) | 1.8171 |  | Correlated to: lab 1925 2420.dat |  |  | % | 120.7 / 132.0
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 9192.5672 | 0.037792 | 0.64459
IM/IW | 0.21619 | I*R1/E | 0.0068534 | Rosenberg | 1211.5644 | % | 306.3 / 219.3
IW*X/E | 0.15474 | I*R2/E | 0.0058529 | Schwisky | 1735.3514 | Amps | 1980.551 |  |  | HP0.95 | 2642.1471
SUM | 0.37093 | Friction/OP. | 0.0035858 | Tsurumi | 593.8996 | Max. Output | 8851.9851 | 0.036336 | 0.65813 | HP1.5 | 252982.2128
IH/I | 0.011382 | Total | 0.027674 | Thrust (1mm) | 437.5724 | % | 296.6483 |  |  | (RPM/1000)2.4 | 21.6335
|  | Efficiency | 0.97233 | Thrust (3 mm) | 1116.3624 | Amps | 1941.3059 |  |  | (RPM/1000)1.8 | 10.031
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 27
Slot Number | 46 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.1337 | Coil Cur. Density |  | k | 0.0685
Depth | 38.41 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 142084.276 | 4.49 / 4.67 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 111.5356 | Bar Cur. Den. |  | Load Inertia | 1570.0039
Tip Depth | 3 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 441045.4 | UB: 6.44 / 6.70 | LB: -
Up. Sl. Wid. | 14.12 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.69435 | UER: 4.03 / 4.19 | LER: - |  | 392.501
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.19443 | 0.7 | 130.0001 | 622.6613
0.008 | 108.2793 | 155.3475 | 0.8 | 130.0049 | 626.2086
0.04 | 215 | 474.0758 | 0.9 | 130.0066 | 629.2353
0.091429 | 164.5582 | 558.6011 | 1 | 130 | 631.8458
0.14286 | 141.6478 | 581.2415
0.19429 | 134.0726 | 591.1171 | Acceleration Data (FV / 0.80 V)
0.29714 | 130.7271 | 600.9748 | Load Type: | Fan / Pump
0.4 | 130 | 607.7857 | Load Inertia: | 66.2 kg.m²
0.5 | 130 | 613.5449 | Accel. Time: | 2.1 / 4.0 (s)
0.6 | 130.0001 | 618.4763 | Rated Torque: | 812.1 kg.m
Load | Torque 80% | LRA 80%
100 | 0 | 76.6838
98.4 | 69.2988 | 124.278
89.75 | 137.6 | 379.2607
76.2286 | 105.3172 | 446.8809
62.8571 | 90.6546 | 464.9932
51.2571 | 85.8065 | 472.8937
33.4857 | 83.6653 | 480.7798
22 | 83.2 | 486.2286
14 | 83.2 | 490.8359
8 | 83.2 | 494.781
6 | 83.2001 | 498.129
8 | 83.2031 | 500.9669
15 | 83.2042 | 503.3882
30 | 83.2 | 505.4767

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | DT2M80U | [5 empty] | HRW / Model Number: | M803WTQL11F-C
Type: TIKE - Form: DCW - 2 Pole - 4000 HP - 4000 V - 60 Hz - 6813USS - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | NCB1 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 3.5 |  | No load amps |  |  |  | 92 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 820 |  | No load watts |  |  |  | 54644 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 5 |  | Impedance amps |  | 1 | f | 865 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.081"x.258")x2 |  | Impedance volts |  | 1 | f | 1150 | - |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | (.081"x.258")x2 |  | Impedance watts |  | 1 | f | 112057 | - |  | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [6 empty] | Dry Kiln
Connection |  | 2 x Wye |  |  | Winding |  | 80/115 | 49 / 65 | -
MCL |  | 1687 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 14.702 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.7936 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 20 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 493 |  | 3204.5
Coil grouping |  | - |  |  |  | RPM |  | 3585
Coil pitch (slot number) |  | 1 ~ 18 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.0251 |  |  |  | DESIGN |  |  |  |  | Skip
Coil Weight | Wire1 | 469.4 |  |  |  | Nom.Eff. (%): |  |  |  |  | Adjacent
(lbs.) | Wire2 | 469.4 |  |  |  | Min.Eff. (%): |  |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | 90.5
FL / LR |  | 467 / 2951 | 670 / 419
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 3115 | - | 631.8458
[6 empty] | LRT (%) | 60 | 132 | -
[6 empty] | BDT (%) | 175 | 219 | -
[6 empty] | SLIP (%) |  | 0.29 | -
[5 empty] | IEEE-B | Eff. (%) |  | 96.4 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 90.7 | -
|  |  |  | Losses (Watts) |  | Primary |  | 21312 | -
[6 empty] | Secondary |  | 9508 | -
[6 empty] | Core |  | 18324 | -
[6 empty] | F & W |  | 29487 | -
[6 empty] | Stray |  | 31474 | -
End Ring (Reference) |  |  |  | Note
LINK: H15010.RAT & LAB 1925 2420.DAT
RSO2: 400-TB13-03P REF ONLY
TOP HAT ASSY: 135-M127-100
Approved | A. Gracia | Design | J. Dougherty
Date | 2013-03-27 | Date | 2013-03-15 |  | REV0. FIRST ISSUE
REV1. RECORRELATED USING H15010.RAT & LAB 1925 2420.DAT
AS OPPOSED TO H402122.rat & DT2M100_4000_H402122_Lab#1133_byRM.dat
328.0
57.5
62.5
65.5
38.41
3.00
3.00
14.12
5.72
73.0
13.15
17.3
311-
411-
051-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | SULZER PUMPS MEXICO S.A. DE C.V.
| TIC SR No.: | 2372844.1
MOTOR NAMEPLATE DATA
| H.P.: | 4000 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 6813USS |  | ENCL: | WP-II |  | FLAMPS: | 493 |  |  | FLRPM: | 3589
| FORM: | DCW |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40 |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10177158 |  |  |  |  | kW: | -
| NOM. EFF.: | 96.2 |  | MIN. EFF.: |  |  | P.F.: | 90.5
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 3115 |  |  | FULL LOAD (lb-ft.): | 5853 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 130 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 215
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 96.4 | [5 empty] | FULL LOAD: | 90.7
|  | 3/4 LOAD: | 96.2 | [5 empty] | 3/4 LOAD: | 89.7
|  | 1/2 LOAD: | 95.4 | [5 empty] | 1/2 LOAD: | 86.1
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Jerry R
[9 empty] | DATE: | 2025-07-15
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: |  |  |  | FLAmps: | 493
Enclosure: | DCW | Voltage: | 4000 V | Frame: | 6813USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 4000 | Rotor Inertia: | 661.7 lb-ft² | Date: | 2025-07-15
FLRPM: | 3585 | Load Inertia: | 392.5 lb-ft² | File: | DT2M80U
| Locked Rotor Amps: | 3115 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 130% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 215% | Accel. Time: | 2 / 4 (s)
| Rated Torque: | 5860 lb-ft
Comments: |  |  |  | D.E.Curve #:
|  | Prepared by: |  | Checked by:
|  |  | Load | Torque 80% | LRA 80%
100 | 0 | 0.19443 | 100 | 0 | 76.6838
99.2 | 108.2793 | 155.3475 | 98.4 | 69.2988 | 124.278
96 | 215 | 474.0758 | 89.75 | 137.6 | 379.2607
90.8571 | 164.5582 | 558.6011 | 76.2286 | 105.3172 | 446.8809
85.7143 | 141.6478 | 581.2415 | 62.8571 | 90.6546 | 464.9932
80.5714 | 134.0726 | 591.1171 | 51.2571 | 85.8065 | 472.8937
70.2857 | 130.7271 | 600.9748 | 33.4857 | 83.6653 | 480.7798
60 | 130 | 607.7857 | 22 | 83.2 | 486.2286
50 | 130 | 613.5449 | 14 | 83.2 | 490.8359
40 | 130.0001 | 618.4763 | 8 | 83.2 | 494.781
30 | 130.0001 | 622.6613 | 6 | 83.2001 | 498.129
20 | 130.0049 | 626.2086 | 8 | 83.2031 | 500.9669
10 | 130.0066 | 629.2353 | 15 | 83.2042 | 503.3882
0 | 130 | 631.8458 | 30 | 83.2 | 505.4767

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: |  |  |  | FLAmps: | 493
Enclosure: | DCW | Voltage: | 4000 V | Frame: | 6813USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 4000 | Rotor Inertia: | 661.7 lb-ft² | Date: | 2025-07-15
FLRPM: | 3585 | Load Inertia: | 392.5 lb-ft² | File: | DT2M80U
Comments: |  |  |  | D.E.Curve #:
|  | Prepared by: |  | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
631.8458 | 15 | 10 |  | 631.8458 | 0.0001 | 505.4767 | 0.0001
600 | 16.6345 | 11.0897 |  | 630.5477 | 0.195 | 504.4381 | 0.39
500 | 23.9538 | 15.9692 |  | 627.7282 | 0.372 | 502.1826 | 0.744
400 | 37.4277 | 24.9518 |  | 624.4422 | 0.543 | 499.5538 | 1.086
300 | 66.5382 |  |  | 620.568 | 0.714 | 496.4544 | 1.428
200 | 149.7109 |  |  | 616.0041 | 0.891 | 492.8032 | 1.782
215 | 129.5498 | 86.3665 |  | 610.6694 | 1.079 | 488.5355 | 2.158
180 | 204.969 | 123.2189 |  | 604.3813 | 1.29 | 483.5051 | 2.58
145 | 284.8246 | 189.8831 |  | 596.0446 | 1.53 | 476.8357 | 3.06
125 |  | 400 |  | 586.1866 | 1.664 | 468.9493 | 3.328
125 |  | 800 |  | 569.9189 | 1.793 | 455.9351 | 3.586
125 |  | 10000 |  | 516.3286 | 1.894 | 413.0629 | 3.788
|  |  |  | 314.7059 | 1.993 | 251.7647 | 3.986
|  |  |  | 120 | 2 | 120 | 4

## StallTime
Rating: | 2 Pole - 4000.0 HP - 3600 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 392.5 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~360 | 130.0 | 22.5 | 0.195 | 3108.6 | 190.4 | 1051.7
360~720 | 130.0 | 11.5 | 0.177 | 3094.7 | 171.3 | 858.7
720~1080 | 130.0 | 7.0 | 0.171 | 3078.5 | 163.5 | 735.3
1080~1440 | 130.0 | 7.0 | 0.171 | 3059.4 | 161.6 | 643.4
1440~1800 | 130.0 | 11.0 | 0.177 | 3036.9 | 164.8 | 570.0
1800~2160 | 130.0 | 18.0 | 0.188 | 3010.6 | 172.3 | 504.7
2160~2530 | 130.4 | 27.7 | 0.211 | 2979.6 | 189.9 | 440.8
2530~2901 | 132.4 | 42.4 | 0.240 | 2938.5 | 211.7 | 375.3
2901~3086 | 137.9 | 57.1 | 0.134 | 2889.9 | 114.0 | 280.4
3086~3271 | 153.1 | 69.5 | 0.129 | 2809.7 | 106.6 | 210.5
3271~3456 | 189.8 | 83.0 | 0.101 | 2545.5 | 77.0 | 122.5
3456~3571 | 161.6 | 94.1 | 0.099 | 1551.5 | 54.6 | 110.6
3571~3579 | 104.1 | 99.2 | 0.092 | 619.2 | 2.2 | 112.5
Acceleration Time: 2.1 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 1780 kW / s |  | 11°C |  | 22°C
Rotor Bar Rise | 4929 kW / s |  | 90°C |  | 181°C
End Ring Rise | 1087 kW / s |  | 33°C |  | 67°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 6.5°C / s |  | 1068.4 kW | 160°C | 24.6 s
Rotor Bar | 58.2°C / s |  | 3178.1 kW | 260°C | 4.5 s
Rotor ER | 21.5°C / s |  | 701.1 kW | 180°C | 8.4 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 50°C + |  | 110°C + | 40°C | = 200°C | 16.9 s
Rotor Bar | 64°C + |  | 196°C + | 40°C | = 300°C | 3.4 s
Rotor ER | 64°C + |  | 116°C + | 40°C | = 220°C | 5.4 s
Cold Stall Time: | 10.4 s |  | Hot Stall Time: |  | 6.7 s

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: |  |  |  | FLAmps: | 493
Enclosure: | DCW | Voltage: | 4000 V | Frame: | 6813USS
Pole: | 2 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 4000 | Rotor Inertia: | 661.7 lb-ft² | Date: | 2025-07-15
FLRPM: | 3585 | Load Inertia: | 392.5 lb-ft² | File: | DT2M80U
| Locked Rotor Amps: | 3115 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 130% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 215% | Accel. Time: | 2.1 / 4.0 (s)
| Rated Torque: | 5860 lb-ft
Comments: |  |  |  | D.E.Curve #:
|  | Prepared by: |  | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 99.804 | 100 | 0.68306
25 | 92.779 | 71.7353 | 161.8827 | 95 | 10.0566
50 | 95.4378 | 86.1445 | 262.0989 | 80 | 19.5529
75 | 96.1527 | 89.7026 | 374.7469 | 71.855 | 29.1113
100 | 96.3592 | 90.7168 | 493.0175 | 44.7528 | 38.7318
125 | 96.3512 | 90.7752 | 615.9267 | 18.1028 | 48.4188
3600
3598
3596
3594
3592
3590
3588
3586
3584
3582
3580
RPM
8000
4000
3200
2400
1600
800
Input Watts (kW)
4800
5600
6400
7200
EFF.
P.F.
RPM
AMPS
WATTS
0

## PERFORMANCE 4160V
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1082
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 2/14/02
[9 empty] | SUPERSEDES |  | NEW
[9 empty] | REVISION |  | 0
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | M. CAMPBELL
API 541 PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | P.A.A
| CUSTOMER: | SULZER PUMPS MEXICO S.A. DE C.V.
| TIC SR No.: | 2372844.1
MOTOR NAMEPLATE DATA
| H.P.: | 4000 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 3600
| FRAME: | 6813USS |  | ENCL: | WP-II |  | FLAMPS: | 493 |  |  | FLRPM: | 3589
| FORM: | DCW |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40 |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10177158 |  |  |  |  | kW: | -
| NOM. EFF.: | 96.2 |  | MIN. EFF.: |  |  | P.F.: | 90.5
LOCKED ROTOR DATA
|  |  | AMPS AT RATED VOLTAGE: | 3115 |  |  |  | POWER FACTOR: | 21.3
|  |  | AMPS AT 80% VOLTAGE: | 2451
TORQUE VALUES | [6 empty] | CURVE NUMBERS
|  |  |  | FULL LOAD (LB.FT): | 5860 |  |  |  | SPEED-TORQUE CURVE: | DT2M80U
|  |  |  | LOCKED ROTOR TORQUE (% OF FLT): | 130 |  |  |  | SPEED-CURRENT CURVE: | DT2M80U
|  |  |  | PULL UP TORQUE (% OF FLT): | 130 |  |  |  | ACCELERATION CURVE: | DT2M80U
|  |  |  | BREAKDOWN TORQUE (% OF FLT): | 215
LOCKED ROTOR WITHSTAND TIMES
COLD CONDITION | [6 empty] | HOT CONDITION
|  | 100% VOLTAGE: | 15 | [5 empty] | 100% VOLTAGE: | 10
|  | 90% VOLTAGE: | 18 | [5 empty] | 90% VOLTAGE: | 12
|  | 80% VOLTAGE: | 23 | [5 empty] | 80% VOLTAGE: | 16
|  | 70% VOLTAGE: | 31 | [5 empty] | 70% VOLTAGE: | 20
DESIGN DATA
|  | MOTOR ROTOR wk2 (LB.FT2): | 661.7 | [5 empty] | NO LOAD CURRENT: | 92
|  | AIR GAP: | 3.5 | [5 empty] | ACCELERATION TIME: | -
LOAD CHARACTERISTICS
|  |  | LOAD |  |  | 1/2 | 3/4 | FULL | 1.15
|  |  | AMPS (A) |  |  | 261.8 | 374.4 | 493 | -
|  |  | EFFICIENCY (%) |  |  | 95.5 | 96.2 | 96.4 | -
|  |  | POWER FACTOR (%) |  |  | 86.1 | 89.6 | 90.7 | -
|  |  | GUARENTEED EFFICIENCY (%) |  |  | - | - | - | -
EFFICIENCY TO BE DETERMINED BY IEEE 112, METHOD B
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2025-07-15
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE, FREQUENCY AND SINEWAVE POWER INPUT.

## Rev. 1
TOSHIBA INTERNATIONAL CORPORATION | [6 empty] | INDEX | MPCF-1109
Industrial Division / Houston Motor Plant | [6 empty] | SHEET NO. | 1 of 1
[7 empty] | ISSUED | 2004-11-18
EQUIVALENT CIRCUIT DATA | [6 empty] | SUPERSEDES | NEW
[7 empty] | REVISION | REV. 0
[7 empty] | WRITTEN BY | MDC
All Values are Presented in Ohms/Phase, Equivalent Wye Connection. | [6 empty] | APPROVED BY | Paul Anderson
| CUSTOMER: | SULZER PUMPS MEXICO S.A. DE C.V.
| TIC SR No.: | 2372844.1
MOTOR NAMEPLATE DATA
| H.P.: | 4000 | VOLTS: | 4000 | 3 PH / | 60 Hz |  | S. RPM: | 3600
| FRAME: | 6813USS | ENCL: | WP-II | FLAMPS: | 493 |  | FLRPM: | 3589
| FORM: | DCW | S.F.: | 1.0 | NEMA DESIGN: | - |  | INSUL CLASS: | F
| TYPE: | TIKE | AMB.: | 40 | CODE: | F |  | DUTY: | Cont.
| MODEL No.: | A1-10177158 |  |  | kW: | -
| NOM. EFF.: | 96.2 | MIN. EFF.: |  | P.F.: | 90.5
Primary Resistance (R1) : |  |  |  | 0.033
Secondary Resistance (R2) : |  |  |  | 0.031
Starting Resistance (R3) : |  |  |  | 0.133
Primary Reactance (X1) : |  |  |  | .651
Secondary Reactance (X2) : |  |  |  | .540
Starting Reactance (X3) : |  |  |  | .316
Magnetizing Reactance (Xm) : |  |  |  | 74.5
Transient Reactance : |  |  |  | 1.188
Sub Transient Reactance : |  |  |  | 0.85
Short Circuit Time Constant : |  |  |  | 0.103
Sub Transient Time Constant : |  |  |  | 0.012
Open Circuit Time Constant : |  |  |  | 6.52
[6 empty] | CERTIFIED BY: | JERRY R
[6 empty] | DATE: | 2025-07-15