## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\Top_Hat_5012\Electric\SERIES DESIGNS\Cu-Bar\WPII\4P\DT4450K.rat |  |  |  |  | Date: | 2020-07-09 | Time: | 15:03
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
4 | 450 | 1800 | DCKW | 4000 | 60 | 105 | 1777.1 / 1774.5 | 0.0127 / 0.0142 | 5011/12
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 20.4203 | LR Test Data
Air Gap | 1.7 | [5 empty] | Rt. Slot Pitch | 27.6032 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 14 | Cross Section Area |  | Mean Value | 24.0117 | 755.8412
Core Length | 305 | 305 |  |  | UB: 200.0 | UER: 1375.0 | Eff.T.W.St. | 12.4165 | WS
OD | 590 | 386.6 | Coil Pitch | 0.86658 |  |  | Eff.T.W.Rt. | 26.8488 | 21198.6583
ID | 390 | 220 | Slot Fill | - | EBL: 40.0 | ERD1: 282.5 | St.Carter Fac. | 1.2245 | IS
Core Depth | 54 | 56.25 | Con./Slot | 21 |  | ERT: 55.00 | Rt.Carter Fac. | 1.0281 | 58.4623
Eff.Core L. | 227.85 | 227.85 | Wire Size 1 | (.057"x.162")x2 | (8 x 25) | ERH: 25.00 | Carter Factor | 1.2589 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.97812 | 10.9975
Number | 60 | 44 | // Circuits | 1 |  |  | Distrib. Factor | 0.95651 | AC
Kind | Open | Rectang | Connection | Wye |  |  | Wind. Factor | 0.93558 | 601.2188
Skew | - | 0 | MCL | 780 | 440 |  | Reactance | (Coeff.: 0.1167)
Depth | 46 | 27.05 | No.Cond./Ph. | 420 |  |  |  | Running | Start
Width | 8.00 - 8.00 | 8.05 | Res. (20°C) | 0.50517 |  |  | Stator Slot | 17.9179 | 17.9179
Opening | 11.6 | 3 | (105°C) | 0.67389 | 0.54526 | 0.031016 | Rotor Slot | 18.3402 | 13.9276
Tip Depth | 2.83 | 2 | Material | CU | CU | CU | Zigzag | 7.4955 | 4.9915
T.Min.Wid. | 8.8203 | 15.6908 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 21.0975 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 5.3124 | 3.6121
Up. R. | - | 0.8 | Weight (kg) |  |  |  | Total Resist. | 1.2502 | 2.0674
Wedge Dep. | 2.40 - 2.00 | Magnetic | Wire 1 | 98.7008 | 38.7248 | 23.6172 | Total React. | 8.1867 | 7.1726
Duct | 6 x 10 | 6 x 10 | Wire 2 | - | - | - | Impedance | 8.2816 | 7.4646
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 25.041 |  | Length | Section | Density | AT | Volume | Loss |  | 1768.5 | 125RPM
| Reac.= | 25.0474 | Primary Core | 23.1692 | 246.078 | 17.9311 | 648.8899 | 20718.4423 | 1893.0555 |  | 1774.5 | 100RPM
Excitation Data |  |  | Tooth | 4.6 | 301.457 | 14.6371 | 47.4449 | 5546.8086 | 364.7895 |  | 1780.5 | 75RPM
Excit.Amps | 19.215 / 16.458 |  | Second.Core | 13.0572 | 256.3313 | 17.2138 | 298.1805 | Total | 2257.8449 |  | 1786.2 | 50RPM
Core Loss | 0.621 / 0.532 | Flux / Pole | Tooth | 2.705 | 393.2656 | 11.22 | 12.23 | C.L.C. | 1.50 / 1.23 |  | 1791.8 | 25RPM
NoLoad | 19.23 / 16.47 | 4.4124 | Air Gap | 0.17 | 596.1026 | 7.4022 | 1001.3769 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 71 / 65 |  | No Load Loss | 6469.0 / 7538.1 | W.Loss | 3386.8 / 2787.5
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 6909.8 / 7200.1 | S.Loss | 922.6 / 759.4
Current (A) | 24.47 / 24.55 | 33.66 / 33.78 | 45.39 / 45.55 | 58.46 / 58.66 | 72.59 / 72.84 | Second. Loss | 4506.6 / 3658.5 | Total C.Loss | 4309.4 / 3546.8
Efficiency | 0.920 / 0.899 | 0.949 / 0.927 | 0.954 / 0.932 | 0.953 / 0.931 | 0.949 / 0.927 | Frict.& Wind. | 1600.0 / 4783.2 | Stray Loss | 5719.0176 | 0.953 | 0.931 | 0.97692 | Eff.
P.F. | 0.538 / 0.549 | 0.758 / 0.773 | 0.839 / 0.856 | 0.870 / 0.887 | 0.880 / 0.897 | Starting Data |  | Slip | PF | 0.870 | 0.887 | 1.0195 | PF.
Slip | 0.0032 / 0.0046 | 0.0063 / 0.0077 | 0.0094 / 0.0109 | 0.0127 / 0.0142 | 0.0161 / 0.0175 | LRA | 309.4 / 352.8 |  |  | 58.46 | 58.66 | 1.0034 | Current
RPM | 1794.3 / 1791.8 | 1788.7 / 1786.2 | 1783.0 / 1780.5 | 1777.1 / 1774.5 | 1771.1 / 1768.5 | % | 529.2 / 603.5 |  |  | 1777.1 | 1774.5 | 0.99854 | RPM
L (Inv., MH) | 16.5298 | 16.5298 | 16.5298 | 16.5167 | 16.407 | LRT (kg.m) | 217.0 / 250.1 |  | 0.27698
(No Load) | 16.5298 |  | Correlated to: H202029_WPII_Lab8343B.dat |  |  | % | 117.9 / 135.9
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 839.8484 | 0.070154 | 0.58976
IM/IW | 0.37636 | I*R1/E | 0.016929 | Rosenberg | 365.4983 | % | 247.0 / 275.8
IW*X/E | 0.18099 | I*R2/E | 0.01274 | Schwisky | 644.0433 | Amps | 191.1179 |  |  | HP0.95 | 331.5522
SUM | 0.55734 | Friction/OP. | 0.0047662 | Tsurumi | 518.8814 | Max. Output | 783.1502 | 0.065058 | 0.61498 | HP1.5 | 9545.9421
IH/I | 0.01071 | Total | 0.045145 | Thrust (1mm) | 106.0184 | % | 233.2887 |  |  | (RPM/1000)2.4 | 4.0988
|  | Efficiency | 0.95485 | Thrust (3 mm) | 212.2569 | Amps | 183.8036 |  |  | (RPM/1000)1.8 | 2.8807
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 24
Slot Number | 44 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.1252 | Coil Cur. Density |  | k | 0.0685
Depth | 27.05 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 36617.5922 | 5.18 / 5.19 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 20.7968 | Bar Cur. Den. |  | Load Inertia | 1714.3773
Tip Depth | 2 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 85284.5 | UB: 6.84 / 6.86 | LB: -
Up. Sl. Wid. | 8.05 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.89993 | UER: 3.50 / 3.51 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.27909 | 0.69 | 136.0328 | 581.2166
0.007 | 72.3117 | 79.2402 | 0.79333 | 135.4906 | 587.5648
0.035 | 250.6027 | 294.1588 | 0.89667 | 135.1774 | 593.2349
0.07 | 275 | 428.2845 | 1 | 135 | 598.3051
0.12167 | 198.4449 | 485.6448
0.17333 | 170.673 | 513.9199 | Acceleration Data (FV / 0.80 V)
0.27667 | 150.4927 | 541.1222 | Load Type: | Fan / Pump
0.38 | 142.3438 | 555.4576 | Load Inertia: | 25.7 kg.m²
0.48333 | 138.7498 | 565.6615 | Accel. Time: | 1.0 / 1.8 (s)
0.58667 | 136.9882 | 574.0673 | Rated Torque: | 184.0 kg.m
Load | Torque 80% | LRA 80%
100 | 0 | 13.173
98.6 | 46.2795 | 63.3922
91.125 | 160.3857 | 235.3271
81.8 | 176 | 342.6276
68.3667 | 127.0047 | 388.5159
55.8667 | 109.2307 | 411.1359
36.9667 | 96.3153 | 432.8978
24.2 | 91.1 | 444.3661
15.3333 | 88.7999 | 452.5292
8.8 | 87.6725 | 459.2538
6.2 | 87.061 | 464.9733
7.8667 | 86.714 | 470.0518
14.7667 | 86.5135 | 474.588
30 | 86.4 | 478.644

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | DT4450K | [5 empty] | HRW / Model Number: | 4504WTAK11F-C
Type: TIKE - Form: DCKW - 4 Pole - 450 HP - 4000 V - 60 Hz - 5011/12 - Class F | [11 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  |  | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [7 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 1.7 |  | No load amps |  |  |  | 16.5 | - |  |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 305 |  | No load watts |  |  |  | 7538 | - |  |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 10,11 |  | Impedance amps |  | 3 | f | 89 | - |  |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.057"x.162")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 21199 | - |  |  | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) |  |  |  | RM |  | RTD 1.0SF |  | Dry Kiln
Connection |  | 1 x Wye |  |  | Winding |  | 80/115 | 71 / 94 | - | 81.2855
MCL |  | 780 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 8.5662 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 2.9704 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 21 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 59 |  |  | 383.5
Coil grouping |  | - |  |  |  | RPM |  | 1775
Coil pitch (slot number) |  | 1 ~ 14 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.5052 |  |  |  | DESIGN |  | B |  |  |  | Skip
Coil Weight | Wire1 | 217.1 |  |  |  | Nom.Eff. (%): |  | - |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 519 / 3105 | 686 / 351
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | 374 | 353 | - |  | 598.3051
[6 empty] | LRT (%) | 80 | 135 | -
[6 empty] | BDT (%) | 175 | 275 | -
[6 empty] | SLIP (%) |  | 1.42 | -
[5 empty] | IEEE-B | Eff. (%) |  | 93.1 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 88.7 | -
|  |  |  | Losses (Watts) |  | Primary |  | 7200 | -
[6 empty] | Secondary |  | 3659 | -
[6 empty] | Core |  | 3547 | -
[6 empty] | F & W |  | 4783 | -
[6 empty] | Stray |  | 5719 | -
End Ring (Reference) |  |  |  | Note
Approved |  | Design | H. Yamaga
Date |  | Date | 2004-11-03
27.05
2.00
3.00
8.05
46.0
2.83
11.6
282.5
25.0
40.0
55.0
311-
411-
051-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 4 Pole - 450.0 HP - 1800 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 152.4 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~186 | 135.1 | 22.4 | 0.111 | 351.5 | 28.0 | 60.6
186~372 | 135.3 | 11.3 | 0.101 | 348.3 | 25.0 | 49.4
372~558 | 135.8 | 7.0 | 0.097 | 344.8 | 23.7 | 42.2
558~744 | 136.5 | 7.5 | 0.097 | 340.8 | 23.1 | 36.8
744~930 | 137.9 | 12.1 | 0.100 | 336.2 | 23.1 | 32.3
930~1116 | 140.5 | 19.8 | 0.104 | 330.7 | 23.4 | 28.1
1116~1302 | 146.4 | 30.6 | 0.108 | 323.5 | 23.5 | 23.6
1302~1488 | 160.6 | 46.4 | 0.110 | 311.2 | 22.6 | 18.4
1488~1581 | 184.6 | 62.1 | 0.051 | 294.9 | 9.5 | 12.2
1581~1674 | 236.7 | 75.1 | 0.039 | 269.6 | 6.4 | 7.6
1674~1737 | 262.8 | 86.5 | 0.024 | 213.1 | 3.1 | 5.5
1737~1777 | 175.3 | 94.9 | 0.034 | 110.2 | 0.2 | 2.0
Acceleration Time: 1.0 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 212 kW / s |  | 6°C |  | 11°C
Rotor Bar Rise | 302 kW / s |  | 20°C |  | 40°C
End Ring Rise | 17 kW / s |  | 2°C |  | 4°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 7.8°C / s |  | 296.6 kW | 160°C | 20.5 s
Rotor Bar | 28.8°C / s |  | 428.8 kW | 260°C | 9.0 s
Rotor ER | 2.7°C / s |  | 24.4 kW | 180°C | 67.1 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 71°C + |  | 89°C + | 40°C | = 200°C | 11.4 s
Rotor Bar | 95°C + |  | 165°C + | 40°C | = 300°C | 5.7 s
Rotor ER | 95°C + |  | 85°C + | 40°C | = 220°C | 31.6 s
Cold Stall Time: | 22.1 s |  | Hot Stall Time: |  | 10.4 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | SULZER PUMPS MEXICO S.A. DE C.V.
| TIC SR No.: | 2182344.3
MOTOR NAMEPLATE DATA
| H.P.: | 450 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1800
| FRAME: | 5012US |  | ENCL: | WP-II |  | FLAMPS: | 59 |  |  | FLRPM: | 1775
| FORM: | DCW4 |  | S.F.: | 1.0 |  | NEMA DESIGN: | B |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10033109 |  |  |  |  | kW: | 336
| NOM. EFF.: | 93 |  | MIN. EFF.: | - |  | P.F.: | 88.5
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 353 |  |  | FULL LOAD (lb-ft.): | 1332 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 135 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 275
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 93.1 | [5 empty] | FULL LOAD: | 88.7
|  | 3/4 LOAD: | 93.2 | [5 empty] | 3/4 LOAD: | 85.6
|  | 1/2 LOAD: | 92.7 | [5 empty] | 1/2 LOAD: | 77.3
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2020-07-09
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | A1-10033109 |  |  | FLAmps: | 59
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 450 | Rotor Inertia: | 123.4 lb-ft² | Date: | 2020-07-09
FLRPM: | 1775 | Load Inertia: | 152.4 lb-ft² | File: | DT4450K
| Locked Rotor Amps: | 353 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 135% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 275% | Accel. Time: | 1.0 / 1.8 (s)
| Rated Torque: | 1332 lb-ft
Comments: | PROJECT | 2182344.3 |  | D.E.Curve #: | DT4450K
|  | Prepared by: | Zichao Xie | Checked by:
|  |  | Load | Torque 80% | LRA 80%
100 | 0 | 0.27909 | 100 | 0 | 13.173
99.3 | 72.3117 | 79.2402 | 98.6 | 46.2795 | 63.3922
96.5 | 250.6027 | 294.1588 | 91.125 | 160.3857 | 235.3271
93 | 275 | 428.2845 | 81.8 | 176 | 342.6276
87.8333 | 198.4449 | 485.6448 | 68.3667 | 127.0047 | 388.5159
82.6667 | 170.673 | 513.9199 | 55.8667 | 109.2307 | 411.1359
72.3333 | 150.4927 | 541.1222 | 36.9667 | 96.3153 | 432.8978
62 | 142.3438 | 555.4576 | 24.2 | 91.1 | 444.3661
51.6667 | 138.7498 | 565.6615 | 15.3333 | 88.7999 | 452.5292
41.3333 | 136.9882 | 574.0673 | 8.8 | 87.6725 | 459.2538
31 | 136.0328 | 581.2166 | 6.2 | 87.061 | 464.9733
20.6667 | 135.4906 | 587.5648 | 7.8667 | 86.714 | 470.0518
10.3333 | 135.1774 | 593.2349 | 14.7667 | 86.5135 | 474.588
0 | 135 | 598.3051 | 30 | 86.4 | 478.644

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | A1-10033109 |  |  | FLAmps: | 59
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 450 | Rotor Inertia: | 123.4 lb-ft² | Date: | 2020-07-09
FLRPM: | 1775 | Load Inertia: | 152.4 lb-ft² | File: | DT4450K
353 A
135%
1332 lb-ft
Comments: | PROJECT | 2182344.3 |  | D.E.Curve #: | DT4450K
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time | CURRENT (%) | Accel. Time
598.3051 | 31.6141 | 14.8818 |  | 598.3051 | 0.0001 | 598.3051 | 0.0001
532.8766 | 39.854 | 18.7606 |  | 476.6102 | 0.195 | 595.7627 | 0.111
467.4285 | 51.7959 | 24.382 |  | 472.3729 | 0.361 | 590.339 | 0.212
402 | 70.0283 | 32.9646 |  | 467.4576 | 0.518 | 584.4068 | 0.309
302 | 124.0828 |  |  | 462.0339 | 0.675 | 577.6271 | 0.406
202 | 277.3466 |  |  | 455.9322 | 0.839 | 569.8305 | 0.506
275 | 149.6443 | 70.4425 |  | 448.4746 | 1.018 | 560.5085 | 0.61
180 | 440.3243 | 164.4203 |  | 438.6441 | 1.217 | 548.3051 | 0.718
120 | 785.8924 | 369.9457 |  | 422.0339 | 1.439 | 527.4576 | 0.828
110 |  | 800 |  | 399.8305 | 1.551 | 499.8305 | 0.879
110 |  | 1600 |  | 365.5932 | 1.633 | 456.9492 | 0.918
110 |  | 10000 |  | 288.9831 | 1.685 | 361.1864 | 0.942
|  |  |  | 186.7797 | 1.761 | 186.7797 | 0.976

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | A1-10033109 |  |  | FLAmps: | 59
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 450 | Rotor Inertia: | 123.4 lb-ft² | Date: | 2020-07-09
FLRPM: | 1775 | Load Inertia: | 152.4 lb-ft² | File: | DT4450K
| Locked Rotor Amps: | 353 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 135% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 275% | Accel. Time: | 1.0 / 1.8 (s)
| Rated Torque: | 1332 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 1800 | 1000
[8 empty] | 1796 | 900
Comments: | PROJECT | 2182344.3 |  | D.E.Curve #: | DT4450K |  |  | 1792 | 800
[8 empty] | 1788 | 700
[8 empty] | 1784 | 600
[8 empty] | 1780 | 500
|  | Prepared by: | Zichao Xie | Checked by: |  | SYNC SPEED | 1800 | 1776 | 400
[6 empty] | NEW SPEED LOWER RANGE | 1760 | 1772 | 300
[6 empty] | NEW kW UPPER RANGE | 1000 | 1768 | 200
[8 empty] | 1764 | 100
[8 empty] | 1760 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 16.5 | 100 | 0.7538
25 | 89.9 | 54.9 | 24.55 | 85.3939 | 9.3378
50 | 92.7 | 77.3 | 33.78 | 69.8006 | 18.0909
75 | 93.2 | 85.6 | 45.55 | 53.9276 | 27.0136
100 | 93.1 | 88.7 | 58.66 | 37.5 | 36.0484
125 | 92.7 | 89.7 | 72.84 | 20.7919 | 45.2671
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 16.5223 | 100 | 6.6175
25 | 89.8727 | 54.863 | 24.5504 | 79.075 | 9.3314
50 | 92.6941 | 77.3223 | 33.7784 | 65.167 | 18.0947
75 | 93.1883 | 85.5581 | 45.5474 | 50.8457 | 26.9981
100 | 93.0602 | 88.6974 | 58.6611 | 36.0064 | 36.047
125 | 92.6618 | 89.6721 | 72.8412 | 20.9876 | 45.2525
1800
1796
1792
1788
1784
1780
1776
1772
1768
1764
1760
RPM
1000
500
400
300
200
100
Input Watts (kW)
600
700
800
900
EFF.
P.F.
RPM
AMPS
WATTS
0.0

## Circuit Param
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | INDEX | MPCF-1109
Industrial Division / Houston Motor Plant | [7 empty] | SHEET NO. | 1 of 1
[8 empty] | ISSUED | 2004-11-18
EQUIVALENT CIRCUIT DATA | [7 empty] | SUPERSEDES | NEW
[8 empty] | REVISION | REV. 0
[8 empty] | WRITTEN BY | MDC
All Values are Presented in Ohms/Phase, Equivalent Wye Connection. | [7 empty] | APPROVED BY | Paul Anderson
| CUSTOMER: | SULZER PUMPS MEXICO S.A. DE C.V.
| TIC SR No.: | 2182344.3
MOTOR NAMEPLATE DATA
| H.P.: | 450 | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  | S. RPM: | 1800
| FRAME: | 5012US | ENCL: | WP-II |  | FLAMPS: | 59 |  | FLRPM: | 1775
| FORM: | DCW4 | S.F.: | 1.0 |  | NEMA DESIGN: | B |  | INSUL CLASS: | F
| TYPE: | TIKE | AMB.: | 40°C |  | CODE: | F |  | DUTY: | Cont.
| MODEL No.: | A1-10033109 |  |  |  | kW: | 336
| NOM. EFF.: | 93 | MIN. EFF.: | - |  | P.F.: | 88.5
Primary Resistance (R1) : |  |  |  |  | 0.67389
Secondary Resistance (R2) : |  |  |  |  | 0.57627
Starting Secondary Resistance (R3) : |  |  |  |  | 1.3936
Primary Reactance (X1) : |  |  |  |  | 4.0113
Secondary Reactance (X2) : |  |  |  |  | 3.3205
Starting Secondary Reactance (X3) : |  |  |  |  | 2.9039
Magnetizing Reactance (Xm) : |  |  |  |  | 140.2186
Transient Reactance : |  |  |  |  | 7.255
Sub Transient Reactance : |  |  |  |  | 5.5435
Short Circuit Time Constant : |  |  |  |  | 3.3385
Sub Transient Time Constant : |  |  |  |  | 0.0089413
Open Circuit Time Constant : |  |  |  |  | 0.66071
[7 empty] | CERTIFIED BY: | Zichao Xie
[7 empty] | DATE: | 2020-07-09

## Performance API
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1082
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 2/14/02
[9 empty] | SUPERSEDES |  | NEW
[9 empty] | REVISION |  | 0
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | M. CAMPBELL
API 541 PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | P.A.A
| CUSTOMER: | SULZER PUMPS MEXICO S.A. DE C.V.
| TIC SR No.: | 2182344.3
MOTOR NAMEPLATE DATA
| H.P.: | 450 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1800
| FRAME: | 5012US |  | ENCL: | WP-II |  | FLAMPS: | 59 |  |  | FLRPM: | 1775
| FORM: | DCW4 |  | S.F.: | 1.0 |  | NEMA DESIGN: | B |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10033109 |  |  |  |  | kW: | 336
| NOM. EFF.: | 93 |  | MIN. EFF.: | - |  | P.F.: | 88.5
LOCKED ROTOR DATA
|  |  | AMPS AT RATED VOLTAGE: | 353 A |  |  |  | POWER FACTOR: | 26.2%
|  |  | AMPS AT 80% VOLTAGE: | 276 A
TORQUE VALUES | [6 empty] | CURVE NUMBERS
|  |  |  | FULL LOAD (LB.FT): | 1332 |  |  |  | SPEED-TORQUE CURVE: | DT4450K
|  |  |  | LOCKED ROTOR TORQUE (% OF FLT): | 135 |  |  |  | SPEED-CURRENT CURVE: | DT4450K
|  |  |  | PULL UP TORQUE (% OF FLT): | 135 |  |  |  | ACCELERATION CURVE: | DT4450K
|  |  |  | BREAKDOWN TORQUE (% OF FLT): | 275
LOCKED ROTOR WITHSTAND TIMES
COLD CONDITION | [6 empty] | HOT CONDITION
|  | 100% VOLTAGE: | 31 (s) | [5 empty] | 100% VOLTAGE: | 14 (s)
|  | 90% VOLTAGE: | 39 (s) | [5 empty] | 90% VOLTAGE: | 18 (s)
|  | 80% VOLTAGE: | 49 (s) | [5 empty] | 80% VOLTAGE: | 23 (s)
|  | 70% VOLTAGE: | 64 (s) | [5 empty] | 70% VOLTAGE: | 30 (s)
DESIGN DATA
|  | MOTOR ROTOR wk2 (LB.FT2): | 123.4 | [5 empty] | NO LOAD CURRENT: | 16.47 A
|  | AIR GAP: | 1.7 mm | [5 empty] | ACCELERATION TIME: | 1 / 2 (s)
LOAD CHARACTERISTICS
|  |  | LOAD |  |  | 1/2 | 3/4 | FULL | SF
|  |  | AMPS (A) |  |  | 33.78 | 45.55 | 58.66 | -
|  |  | EFFICIENCY (%) |  |  | 92.7 | 93.2 | 93.1 | -
|  |  | POWER FACTOR (%) |  |  | 77.3 | 85.6 | 88.7 | -
|  |  | GUARENTEED EFFICIENCY (%) |  |  | - | - | - | -
EFFICIENCY TO BE DETERMINED BY IEEE 112, METHOD B
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2020-07-09
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE, FREQUENCY AND SINEWAVE POWER INPUT.