## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | N:\DESPRO\RAT FILES\DT4700K.rat |  |  |  |  | Date: | 2020-08-03 | Time: | 11:07
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
4 | 700 | 1800 | DCKW | 4000 | 60 | 105 | 1776.4 / 1773.9 | 0.0131 / 0.0145 | 5011/12
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 20.4203 | LR Test Data
Air Gap | 1.7 | [5 empty] | Rt. Slot Pitch | 27.6032 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 14 | Cross Section Area |  | Mean Value | 24.0117 | 725.3981
Core Length | 530 | 530 |  |  | UB: 200.0 | UER: 1375.0 | Eff.T.W.St. | 12.4165 | WS
OD | 590 | 386.6 | Coil Pitch | 0.86658 |  |  | Eff.T.W.Rt. | 26.8488 | 29663.9673
ID | 390 | 220 | Slot Fill | - | EBL: 40.0 | ERD1: 282.5 | St.Carter Fac. | 1.2245 | IS
Core Depth | 54 | 56.25 | Con./Slot | 14 |  | ERT: 55.00 | Rt.Carter Fac. | 1.0281 | 86.2281
Eff.Core L. | 390.6 | 390.6 | Wire Size 1 | (.081"x.162")x2 | (8 x 25) | ERH: 25.00 | Carter Factor | 1.2589 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.97812 | 16.4962
Number | 60 | 44 | // Circuits | 1 |  |  | Distrib. Factor | 0.95651 | AC
Kind | Open | Rectang | Connection | Wye |  |  | Wind. Factor | 0.93558 | 591.1725
Skew | - | 0 | MCL | 1005 | 665 |  | Reactance | (Coeff.: 0.0889)
Depth | 46 | 27.05 | No.Cond./Ph. | 280 |  |  |  | Running | Start
Width | 8.00 - 8.00 | 8.05 | Res. (20°C) | 0.30049 |  |  | Stator Slot | 17.9179 | 17.9179
Opening | 11.6 | 3 | (105°C) | 0.40084 | 0.36626 | 0.013785 | Rotor Slot | 18.3402 | 13.9276
Tip Depth | 2.83 | 2 | Material | CU | CU | CU | Zigzag | 7.4955 | 4.9137
T.Min.Wid. | 8.8203 | 15.6908 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 12.3069 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 5.3124 | 3.5775
Up. R. | - | 0.8 | Weight (kg) |  |  |  | Total Resist. | 0.78089 | 1.3299
Wedge Dep. | 2.40 - 2.00 | Magnetic | Wire 1 | 122.432 | 56.327 | 23.6172 | Total React. | 5.456 | 4.6715
Duct | 11 x 10 | 11 x 10 | Wire 2 | - | - | - | Impedance | 5.5116 | 4.8571
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 25.041 |  | Length | Section | Density | AT | Volume | Loss |  | 1767.7 | 125RPM
| Reac.= | 25.0474 | Primary Core | 23.1692 | 421.848 | 15.6897 | 330.9878 | 35517.3292 | 2613.964 |  | 1773.9 | 100RPM
Excitation Data |  |  | Tooth | 4.6 | 516.7834 | 12.8074 | 31.7811 | 9508.8146 | 503.7076 |  | 1780.1 | 75RPM
Excit.Amps | 20.099 / 17.215 |  | Second.Core | 13.0572 | 439.425 | 15.0621 | 153.13 | Total | 3117.6716 |  | 1786.0 | 50RPM
Core Loss | 0.842 / 0.721 | Flux / Pole | Tooth | 2.705 | 674.1696 | 9.8175 | 8.2252 | C.L.C. | 1.50 / 1.23 |  | 1791.7 | 25RPM
NoLoad | 20.12 / 17.23 | 6.6187 | Air Gap | 0.17 | 1021.8902 | 6.4769 | 876.2048 | S.F.C. | 6.05
Load Characteristics |  |  | Temp. Rise @ 100%: | 75 / 71 |  | No Load Loss | 7804.1 / 9093.9 | W.Loss | 4676.5 / 3849.0
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 8941.2 / 9316.9 | S.Loss | 1163.4 / 957.5
Current (A) | 29.68 / 29.69 | 46.16 / 46.18 | 65.45 / 65.47 | 86.23 / 86.27 | 108.36 / 108.40 | Second. Loss | 7227.7 / 5867.5 | Total C.Loss | 5839.9 / 4806.5
Efficiency | 0.937 / 0.918 | 0.958 / 0.939 | 0.960 / 0.941 | 0.958 / 0.939 | 0.954 / 0.935 | Frict.& Wind. | 1600.0 / 4783.2 | Stray Loss | 9172.166 | 0.958 | 0.939 | 0.98017 | Eff.
P.F. | 0.678 / 0.691 | 0.852 / 0.869 | 0.899 / 0.917 | 0.912 / 0.930 | 0.912 / 0.930 | Starting Data |  | Slip | PF | 0.912 | 0.930 | 1.0197 | PF.
Slip | 0.0032 / 0.0046 | 0.0064 / 0.0078 | 0.0096 / 0.0110 | 0.0131 / 0.0145 | 0.0165 / 0.0179 | LRA | 475.5 / 542.3 |  |  | 86.23 | 86 | 0.99733 | Current
RPM | 1794.3 / 1791.7 | 1788.5 / 1786.0 | 1782.7 / 1780.1 | 1776.4 / 1773.9 | 1770.3 / 1767.7 | % | 551.4 / 628.9 |  |  | 1776.4 | 1770 | 0.9964 | RPM
L (Inv., MH) | 11.0132 | 11.0132 | 11.0132 | 11.0001 | 10.9134 | LRT (kg.m) | 341.7 / 393.8 |  | 0.27381
(No Load) | 11.0132 |  | Correlated to: H202029_WPII_Lab8343B.dat |  |  | % | 119.3 / 137.5
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1298.6514 | 0.069469 | 0.60533
IM/IW | 0.25244 | I*R1/E | 0.015031 | Rosenberg | 479.7165 | % | 245.4 / 274.1
IW*X/E | 0.1881 | I*R2/E | 0.013102 | Schwisky | 845.3069 | Amps | 288.1373 |  |  | HP0.95 | 504.4791
SUM | 0.44054 | Friction/OP. | 0.003064 | Tsurumi | 681.0318 | Max. Output | 1211.7776 | 0.064506 | 0.63073 | HP1.5 | 18520.2598
IH/I | 0.0097235 | Total | 0.04092 | Thrust (1mm) | 139.065 | % | 232.0524 |  |  | (RPM/1000)2.4 | 4.0988
|  | Efficiency | 0.95908 | Thrust (3 mm) | 277.4004 | Amps | 277.2985 |  |  | (RPM/1000)1.8 | 2.8807
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 24
Slot Number | 44 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.12573 | Coil Cur. Density |  | k | 0.0685
Depth | 27.05 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 62773.0152 | 5.29 / 5.29 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 35.6517 | Bar Cur. Den. |  | Load Inertia | 2513.5314
Tip Depth | 2 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 146202 | UB: 7.11 / 7.11 | LB: -
Up. Sl. Wid. | 8.05 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.89993 | UER: 3.63 / 3.64 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.23392 | 0.7 | 135.001 | 609.9889
0.004 | 70.8596 | 78.3132 | 0.8 | 135.0014 | 617.4763
0.02 | 246.1775 | 306.1612 | 0.9 | 135.0043 | 624.1993
0.04 | 270 | 446.4435 | 1 | 135 | 630.2326
0.1 | 191.6441 | 506.0978
0.16 | 163.5635 | 535.7018 | Acceleration Data (FV / 0.80 V)
0.28 | 142.8136 | 564.4897 | Load Type: | Fan / Pump
0.4 | 135 | 580.1855 | Load Inertia: | 103.0 kg.m²
0.5 | 135.0002 | 591.7245 | Accel. Time: | 1.9 / 3.5 (s)
0.6 | 135.0007 | 601.4245 | Rated Torque: | 286.3 kg.m
Load | Torque 80% | LRA 80%
100 | 0 | 16.0935
99.2 | 45.3501 | 62.6505
95.25 | 157.5536 | 244.9289
89.75 | 172.8 | 357.1548
74 | 122.6522 | 404.8783
58.8 | 104.6806 | 428.5614
36.4 | 91.4007 | 451.5918
22 | 86.4 | 464.1484
14 | 86.4001 | 473.3796
8 | 86.4005 | 481.1396
6 | 86.4007 | 487.9911
8 | 86.4009 | 493.981
15 | 86.4028 | 499.3595
30 | 86.4 | 504.1861

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | DT4700K | [5 empty] | HRW / Model Number: | 7004WTAK11F-C
Type: TIKE - Form: DCKW - 4 Pole - 700 HP - 4000 V - 60 Hz - 5011/12 - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 1.7 |  | No load amps |  |  |  | 17.2 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 530 |  | No load watts |  |  |  | 9094 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 7 |  | Impedance amps |  | 3 | f | 137 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (061-0014-07) |  | (.081"x.162")x2 |  | Impedance volts |  | 3 | f | 1150 | - |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 29664 | - |  | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [6 empty] | Dry Kiln
Connection |  | 1 x Wye |  |  | Winding |  | 80/115 | 75 / 99 | -
MCL |  | 1005 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 11.5664 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 2.9704 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 14 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 86 |  | 559
Coil grouping |  | - |  |  |  | RPM |  | 1770
Coil pitch (slot number) |  | 1 ~ 14 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.3005 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 269.4 |  |  |  | Nom.Eff. (%): |  | - |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 529 / 3334 | 711 / 364
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 542 | - | 630.2326
[6 empty] | LRT (%) | 60 | 137 | -
[6 empty] | BDT (%) | 175 | 274 | -
[6 empty] | SLIP (%) |  | 1.45 | -
[5 empty] | IEEE-B | Eff. (%) |  | 93.9 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 93 | -
|  |  |  | Losses (Watts) |  | Primary |  | 9317 | -
[6 empty] | Secondary |  | 5868 | -
[6 empty] | Core |  | 4807 | -
[6 empty] | F & W |  | 4783 | -
[6 empty] | Stray |  | 9172 | -
End Ring (Reference) |  |  |  | Note | DT4700K
LINK: H202029_800HP_4000V(Cu).rat &
H202029_WPII_Lab8343B.dat
361-R311-6L1DY, 361-R311-3L1D, 361-R311-3L1Y
362-R351-02
400-R341-01(RSO2); 135-R321-100 (TOP HAT)
Approved |  | Design | H. Yamaga
Date |  | Date | 2004-11-03 |  | REV0. FIRST ISSUE
27.05
2.00
3.00
8.05
46.0
2.83
11.6
282.5
25.0
40.0
55.0
M
311-
411-
051-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## StallTime
Rating: | 4 Pole - 700.0 HP - 1800 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 611.1 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~180 | 135.0 | 22.5 | 0.207 | 539.4 | 73.0 | 157.2
180~360 | 135.0 | 11.5 | 0.188 | 533.9 | 65.2 | 128.9
360~540 | 135.0 | 7.0 | 0.182 | 527.8 | 61.6 | 110.6
540~720 | 135.0 | 7.0 | 0.182 | 520.9 | 60.1 | 96.7
720~900 | 135.0 | 11.0 | 0.187 | 513.1 | 60.3 | 85.6
900~1080 | 135.0 | 18.0 | 0.199 | 503.9 | 61.9 | 75.6
1080~1296 | 138.9 | 29.2 | 0.254 | 492.2 | 76.1 | 64.5
1296~1512 | 153.2 | 47.6 | 0.264 | 473.1 | 74.9 | 49.6
1512~1620 | 177.6 | 66.4 | 0.125 | 448.0 | 32.0 | 30.8
1620~1728 | 230.8 | 81.9 | 0.094 | 409.6 | 21.3 | 16.9
1728~1764 | 258.1 | 92.5 | 0.028 | 323.6 | 5.0 | 8.5
1764~1776 | 173.1 | 97.2 | 0.021 | 165.3 | 0.2 | 5.6
Acceleration Time: 1.9 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 592 kW / s |  | 13°C |  | 25°C
Rotor Bar Rise | 800 kW / s |  | 37°C |  | 74°C
End Ring Rise | 30 kW / s |  | 3°C |  | 7°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 8.9°C / s |  | 421.3 kW | 160°C | 17.9 s
Rotor Bar | 31.3°C / s |  | 679.4 kW | 260°C | 8.3 s
Rotor ER | 2.8°C / s |  | 25.6 kW | 180°C | 64.0 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 75°C + |  | 85°C + | 40°C | = 200°C | 9.5 s
Rotor Bar | 101°C + |  | 159°C + | 40°C | = 300°C | 5.1 s
Rotor ER | 101°C + |  | 79°C + | 40°C | = 220°C | 27.9 s
Cold Stall Time: | 19.0 s |  | Hot Stall Time: |  | 8.3 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | SULZER PUMPS MEXICO S.A. DE C.V.
| TIC SR No.: | 2182344.8
MOTOR NAMEPLATE DATA
| H.P.: | 700 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1800
| FRAME: | 5012US |  | ENCL: | WP-II |  | FLAMPS: | 86 |  |  | FLRPM: | 1770
| FORM: | DCKW |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10033114 |  |  |  |  | kW: | -
| NOM. EFF.: | 93.6 |  | MIN. EFF.: | - |  | P.F.: | 93
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
LOCKED ROTOR: |  |  | 542 |  |  | FULL LOAD (lb-ft.): | 2077 |  |  | DRIVE END:
[6 empty] | LOCKED ROTOR (%): | 135 |  |  | OPPOSITE DRIVE END:
[6 empty] | BREAK DOWN (%): | 270
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 93.9 | [5 empty] | FULL LOAD: | 93
|  | 3/4 LOAD: | 94.1 | [5 empty] | 3/4 LOAD: | 91.7
|  | 1/2 LOAD: | 93.9 | [5 empty] | 1/2 LOAD: | 86.9
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2020-08-03
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS
Note on L22: Pick bearings from list!

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | A1-10033114 |  |  | FLAmps: | 86 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 211.5 lb-ft² | Date: | 2020-08-03
FLRPM: | 1770 | Load Inertia: | 611.1 lb-ft² | File: | DT4700K
| Locked Rotor Amps: | 542 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 135% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 270% | Accel. Time: | 2 / 4 (s)
| Rated Torque: | 2077 lb-ft
Comments: | PROJECT | 2182344.8 |  | D.E.Curve #: | DT4700K
|  | Prepared by: | JERRY R | Checked by:
|  |  | Load | Torque 80% | LRA 80%
100 | 0 | 0.23392 | 100 | 0 | 16.0935
99.6 | 70.8596 | 78.3132 | 99.2 | 45.3501 | 62.6505
98 | 246.1775 | 306.1612 | 95.25 | 157.5536 | 244.9289
96 | 270 | 446.4435 | 89.75 | 172.8 | 357.1548
90 | 191.6441 | 506.0978 | 74 | 122.6522 | 404.8783
84 | 163.5635 | 535.7018 | 58.8 | 104.6806 | 428.5614
72 | 142.8136 | 564.4897 | 36.4 | 91.4007 | 451.5918
60 | 135 | 580.1855 | 22 | 86.4 | 464.1484
50 | 135.0002 | 591.7245 | 14 | 86.4001 | 473.3796
40 | 135.0007 | 601.4245 | 8 | 86.4005 | 481.1396
30 | 135.001 | 609.9889 | 6 | 86.4007 | 487.9911
20 | 135.0014 | 617.4763 | 8 | 86.4009 | 493.981
10 | 135.0043 | 624.1993 | 15 | 86.4028 | 499.3595
0 | 135 | 630.2326 | 30 | 86.4 | 504.1861

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | A1-10033114 |  |  | FLAmps: | 86 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 211.5 lb-ft² | Date: | 2020-08-03
FLRPM: | 1770 | Load Inertia: | 611.1 lb-ft² | File: | DT4700K
Comments: | PROJECT | 2182344.8 |  | D.E.Curve #: | DT4700K
|  | Prepared by: | JERRY R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
630.2326 | 24 | 12 |  | 630.2326 | 0.0001 | 504.186 | 0.0001
556.829 | 30.7446 | 15.3723 |  | 627.2093 | 0.2144 | 501.7674 | 0.42879
483.4035 | 40.7937 | 20.3969 |  | 620.814 | 0.40911 | 496.6512 | 0.81823
410 | 56.7081 | 28.3541 |  | 613.7209 | 0.59762 | 490.9767 | 1.1952
310 | 99.1949 |  |  | 605.6977 | 0.78612 | 484.5581 | 1.5722
210 | 216.1595 |  |  | 596.6279 | 0.9798 | 477.3023 | 1.9596
270 | 130.7632 | 65.3816 |  | 585.9302 | 1.1859 | 468.7442 | 2.3718
180 | 376.8997 | 147.1085 |  | 572.3256 | 1.449 | 457.8605 | 2.898
145 | 453.3952 | 226.6976 |  | 550.1163 | 1.7224 | 440.093 | 3.4448
125 |  | 500 |  | 520.9302 | 1.8519 | 416.7442 | 3.7038
125 |  | 1000 |  | 476.2791 | 1.9492 | 381.0233 | 3.8985
125 |  | 10000 |  | 376.2791 | 1.9782 | 301.0233 | 3.9565
|  |  |  | 110 | 2 | 110 | 4

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | A1-10033114 |  |  | FLAmps: | 86 A
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5012US
Pole: | 4 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 211.5 lb-ft² | Date: | 2020-08-03
FLRPM: | 1770 | Load Inertia: | 611.1 lb-ft² | File: | DT4700K
| Locked Rotor Amps: | 542 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 135% | Starting at: | FV / 0.80 (V)
| Breakdown Torque: | 270% | Accel. Time: | 2 / 4 (s)
| Rated Torque: | 2077 lb-ft
Comments: | PROJECT | 2182344.8 |  | D.E.Curve #: | DT4700K
|  | Prepared by: | JERRY R | Checked by:
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 20.0626 | 100 | 2
25 | 91.8076 | 69.1202 | 29.5984 | 69.5088 | 10.124
50 | 93.8861 | 86.9119 | 46.0364 | 55.263 | 19.7998
75 | 94.1448 | 91.6998 | 65.2692 | 40.6149 | 29.6181
100 | 93.9012 | 93.0393 | 85.9953 | 25.0524 | 39.5932
125 | 93.4643 | 92.9818 | 108.0633 | 9.7587 | 49.7229
1800
1796
1792
1788
1784
1780
1776
1772
1768
1764
1760
RPM
1400
700
560
420
280
140
Input Watts (kW)
840
980
1120
1260
EFF.
P.F.
RPM
AMPS
WATTS
0

## Circuit Param.
TOSHIBA INTERNATIONAL CORPORATION | [6 empty] | INDEX | MPCF-1109
Industrial Division / Houston Motor Plant | [6 empty] | SHEET NO. | 1 of 1
[7 empty] | ISSUED | 2004-11-18
EQUIVALENT CIRCUIT DATA | [6 empty] | SUPERSEDES | NEW
[7 empty] | REVISION | REV. 0
[7 empty] | WRITTEN BY | MDC
All Values are Presented in Ohms/Phase, Equivalent Wye Connection. | [6 empty] | APPROVED BY | Paul Anderson
| CUSTOMER: | SULZER PUMPS MEXICO S.A. DE C.V.
| TIC SR No.: | 2182344.8
MOTOR NAMEPLATE DATA
| H.P.: | 700 | VOLTS: | 4000 | 3 PH / | 60 Hz |  | S. RPM: | 1800
| FRAME: | 5012US | ENCL: | WP-II | FLAMPS: | 86 |  | FLRPM: | 1770
| FORM: | DCKW | S.F.: | 1.0 | NEMA DESIGN: | - |  | INSUL CLASS: | F
| TYPE: | TIKE | AMB.: | 40°C | CODE: | F |  | DUTY: | Cont.
| MODEL No.: | A1-10033114 |  |  | kW: | -
| NOM. EFF.: | 93.6 | MIN. EFF.: | - | P.F.: | 93
Primary Resistance (R1) : |  |  |  | 0.4008
Secondary Resistance (R2) : |  |  |  | 0.380
Starting Resistance (R3) : |  |  |  | 0.929
Primary Reactance (X1) : |  |  |  | 2.62
Secondary Reactance (X2) : |  |  |  | 2.33
Starting Reactance (X3) : |  |  |  | 1.95
Magnetizing Reactance (Xm) : |  |  |  | 135.8
Transient Reactance : |  |  |  | 4.92
Sub Transient Reactance : |  |  |  | 3.68
Short Circuit Time Constant : |  |  |  | 2.33
Sub Transient Time Constant : |  |  |  | 0.0091
Open Circuit Time Constant : |  |  |  | 0.964
[6 empty] | CERTIFIED BY: | JERRY R
[6 empty] | DATE: | 2020-08-03

## PERFORMANCE data
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1082
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 2/14/02
[9 empty] | SUPERSEDES |  | NEW
[9 empty] | REVISION |  | 0
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | M. CAMPBELL
API 541 PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | P.A.A
| CUSTOMER: | SULZER PUMPS MEXICO S.A. DE C.V.
| TIC SR No.: | 2182344.8
MOTOR NAMEPLATE DATA
| H.P.: | 700 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1800
| FRAME: | 5012US |  | ENCL: | WP-II |  | FLAMPS: | 86 |  |  | FLRPM: | 1770
| FORM: | DCKW |  | S.F.: | 1.0 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | A1-10033114 |  |  |  |  | kW: | -
| NOM. EFF.: | 93.6 |  | MIN. EFF.: | - |  | P.F.: | 93
LOCKED ROTOR DATA
|  |  | AMPS AT RATED VOLTAGE: | 542 |  |  |  | POWER FACTOR: | 25.8
|  |  | AMPS AT 80% VOLTAGE: | 423
TORQUE VALUES | [6 empty] | CURVE NUMBERS
|  |  |  | FULL LOAD (LB.FT): | 2077 |  |  |  | SPEED-TORQUE CURVE: | DT4700K
|  |  |  | LOCKED ROTOR TORQUE (% OF FLT): | 135 |  |  |  | SPEED-CURRENT CURVE: | DT4700K
|  |  |  | PULL UP TORQUE (% OF FLT): | 135 |  |  |  | ACCELERATION CURVE: | DT4700K
|  |  |  | BREAKDOWN TORQUE (% OF FLT): | 270
LOCKED ROTOR WITHSTAND TIMES
COLD CONDITION | [6 empty] | HOT CONDITION
|  | 100% VOLTAGE: | 24 | [5 empty] | 100% VOLTAGE: | 12
|  | 90% VOLTAGE: | 30 | [5 empty] | 90% VOLTAGE: | 15
|  | 80% VOLTAGE: | 38 | [5 empty] | 80% VOLTAGE: | 19
|  | 70% VOLTAGE: | 49 | [5 empty] | 70% VOLTAGE: | 25
DESIGN DATA
|  | MOTOR ROTOR wk2 (LB.FT2): | 211.5 | [5 empty] | NO LOAD CURRENT: | 17
|  | AIR GAP: | 1.7 | [5 empty] | ACCELERATION TIME: | 2 / 4
LOAD CHARACTERISTICS
|  |  | LOAD |  |  | 1/2 | 3/4 | FULL | SF
|  |  | AMPS (A) |  |  | 46.1 | 65.5 | 86 | -
|  |  | EFFICIENCY (%) |  |  | 93.9 | 94.1 | 93.9 | -
|  |  | POWER FACTOR (%) |  |  | 86.9 | 91.7 | 93 | -
|  |  | GUARENTEED EFFICIENCY (%) |  |  | - | - | - | -
EFFICIENCY TO BE DETERMINED BY IEEE 112, METHOD B
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2020-08-03
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE, FREQUENCY AND SINEWAVE POWER INPUT.