## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RAT FILES\DT6700U Rev.1.rat |  |  |  |  | Date: | 2022-04-22 | Time: | 7:55
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
6 | 700 | 1200 | DCK4 | 4000 | 60 | 105 | 1189.4 / 1189.1 | 0.0088 / 0.0091 | 5811/12
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 20.5076 | LR Test Data
Air Gap | 1.6 | [5 empty] | Rt. Slot Pitch | 25.728 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 11 | Cross Section Area |  | Mean Value | 23.1178 | 745.5354
Core Length | 530 | 530 |  |  | UB: 280.0 | UER: 1800.0 | Eff.T.W.St. | 12.9454 | WS
OD | 670 | 466.8 | Coil Pitch | 0.83325 |  |  | Eff.T.W.Rt. | 24.9354 | 29527.905
ID | 470 | 300 | Slot Fill | - | EBL: 45.0 | ERD1: 342.7 | St.Carter Fac. | 1.2095 | IS
Core Depth | 48 | 51.35 | Con./Slot | 26 |  | ERT: 60.00 | Rt.Carter Fac. | 1.0318 | 93.0899
Eff.Core L. | 390.6 | 390.6 | Wire Size 1 | (.051"x.289")x1 | (8 x 30) | ERH: 30.00 | Carter Factor | 1.248 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.96589 | 14.8043
Number | 72 | 57 | // Circuits | 2 |  |  | Distrib. Factor | 0.95749 | AC
Kind | Open | Rectang | Connection | Wye |  |  | Wind. Factor | 0.92484 | 590.1076
Skew | - | 0 | MCL | 936 | 680 |  | Reactance | (Coeff.: 0.0894)
Depth | 52 | 32.05 | No.Cond./Ph. | 312 |  |  |  | Running | Start
Width | 7.56 - 7.56 | 8.05 | Res. (20°C) | 0.27648 |  |  | Stator Slot | 21.0537 | 21.0537
Opening | 10.8 | 3 | (105°C) | 0.36882 | 0.25093 | 0.0071654 | Rotor Slot | 19.0465 | 12.8356
Tip Depth | 2.83 | 2 | Material | CU | CU | CU | Zigzag | 7.7484 | 5.1515
T.Min.Wid. | 9.7076 | 14.146 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 8.3004 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 4.1826 | 2.9498
Up. R. | - | 0.8 | Weight (kg) |  |  |  | Total Resist. | 0.62692 | 1.1358
Wedge Dep. | 2.40 - 2.00 | Magnetic | Wire 1 | 143.3081 | 104.9945 | 37.4725 | Total React. | 5.3954 | 4.4823
Duct | 11 x 10 | 11 x 10 | Wire 2 | - | - | - | Impedance | 5.4317 | 4.624
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 30.0276 |  | Length | Section | Density | AT | Volume | Loss |  | 1186.3 | 125RPM |  | Kline/in2
| Reac.= | 30.0436 | Primary Core | 17.5405 | 374.976 | 16.0245 | 568.7331 | 36636.4491 | 2790.1592 |  | 1189.1 | 100RPM |  | 103.3838
Excitation Data |  |  | Tooth | 5.2 | 455.0147 | 13.2057 | 53.5244 | 14196.4589 | 790.2783 |  | 1191.8 | 75RPM |  | 85.1982
Excit.Amps | 34.261 / 28.449 |  | Second.Core | 10.5427 | 401.1462 | 14.9791 | 188.691 | Total | 3580.4375 |  | 1194.5 | 50RPM |  | 96.6392
Core Loss | 1.091 / 0.906 | Flux / Pole | Tooth | 3.205 | 524.9173 | 11.4472 | 18.1159 | C.L.C. | 1.75 / 0.88 |  | 1197.0 | 25RPM |  | 73.8525
NoLoad | 34.28 / 28.46 | 6.0088 | Air Gap | 0.16 | 828.2227 | 7.2551 | 923.7444 | S.F.C. | 6.05 |  |  |  |  | 46.8068
Load Characteristics |  |  | Temp. Rise @ 100%: | 60 / 54 |  | No Load Loss | 11039.1 / 6190.8 | W.Loss | 6265.8 / 3136.3
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 9588.3 / 8136.9 | S.Loss | 1299.8 / 650.6
Current (A) | 42.20 / 41.73 | 55.54 / 54.93 | 73.16 / 72.36 | 93.09 / 92.06 | 114.75 / 113.48 | Second. Loss | 4827.1 / 4997.5 | Total C.Loss | 7565.5 / 3786.9
Efficiency | 0.914 / 0.907 | 0.948 / 0.940 | 0.956 / 0.948 | 0.957 / 0.949 | 0.954 / 0.947 | Frict.& Wind. | 2500.0 / 1721.8 | Stray Loss | 9494.0537 | 0.957 | 0.949 | 0.99164 | Eff.
P.F. | 0.488 / 0.498 | 0.716 / 0.730 | 0.808 / 0.824 | 0.846 / 0.863 | 0.860 / 0.877 | Starting Data |  | Slip | PF | 0.846 | 0.863 | 1.0201 | PF.
Slip | 0.0022 / 0.0025 | 0.0043 / 0.0046 | 0.0066 / 0.0068 | 0.0088 / 0.0091 | 0.0112 / 0.0114 | LRA | 499.5 / 559.3 |  |  | 93.09 | 92.06 | 0.98894 | Current
RPM | 1197.4 / 1197.0 | 1194.8 / 1194.5 | 1192.1 / 1191.8 | 1189.4 / 1189.1 | 1186.6 / 1186.3 | % | 536.5 / 600.8 |  |  | 1189.4 | 1189.1 | 0.99975 | RPM
L (Inv., MH) | 10.6347 | 10.6347 | 10.6347 | 10.6347 | 10.5606 | LRT (kg.m) | 466.8 / 541.1 |  | 0.24564
(No Load) | 10.6347 |  | Correlated to: LAB 0251.dat |  |  | % | 109.2 / 126.5
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 1276.3073 | 0.047726 | 0.60041
IM/IW | 0.43391 | I*R1/E | 0.014758 | Rosenberg | 725.3843 | % | 242.3 / 258.9
IW*X/E | 0.18446 | I*R2/E | 0.0088239 | Schwisky | 1289.4331 | Amps | 292.1718 |  |  | HP0.95 | 504.4791
SUM | 0.61837 | Friction/OP. | 0.0047874 | Tsurumi | 1047.9795 | Max. Output | 1216.9415 | 0.045362 | 0.61701 | HP1.5 | 18520.2598
IH/I | 0.011804 | Total | 0.040174 | Thrust (1mm) | 209.7529 | % | 233.0413 |  |  | (RPM/1000)2.4 | 1.5489
|  | Efficiency | 0.95983 | Thrust (3 mm) | 408.0053 | Amps | 284.6726 |  |  | (RPM/1000)1.8 | 1.3884
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 24
Slot Number | 57 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.11065 | Coil Cur. Density |  | k | 0.0685
Depth | 32.05 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 91518.9408 | 5.06 / 5.00 |  | Hz | 60
Opening | 3 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 71.7919 | Bar Cur. Den. |  | Load Inertia | 6902.9108
Tip Depth | 2 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 188538 | UB: 4.28 / 4.24 | LB: -
Up. Sl. Wid. | 8.05 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.87494 | UER: 2.02 / 2.00 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.37259 | 0.69684 | 125.8008 | 588.1543
0.008 | 94.7449 | 106.6047 | 0.79789 | 125.3899 | 595.6414
0.04 | 255 | 359.8984 | 0.89895 | 125.1416 | 602.0676
0.090526 | 203.7391 | 466.3767 | 1 | 125 | 607.6087
0.14105 | 163.7202 | 503.0148
0.19158 | 144.6803 | 520.9648 | Acceleration Data (FV V)
0.29263 | 133.1995 | 541.5358 | Load Type: | Fan / Pump
0.39368 | 129.242 | 556.1254 | Load Inertia: | 2022.8 kg.m²
0.49474 | 127.4529 | 568.4694 | Accel. Time: | 14.3 (s)
0.59579 | 126.4253 | 578.8962 | Rated Torque: | 427.6 kg.m
Load
100
98.4
89.75
76.4632
63.3263
51.8526
34.2526
22.6947
14.4211
8.2526
6.0632
7.9579
14.9263
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | DT6700U Rev.1 | [5 empty] | HRW / Model Number: | 7006WTAL11E-C
Type: TIKE - Form: DCK4 - 6 Pole - 700 HP - 4000 V - 60 Hz - 5811/12 - Class F | [10 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  | EPACT | M22 - 26Ga.
Material |  | M22 - 26Ga. |  | NL & Impedance Test | [6 empty] | EQP-III | M36 - 26Ga.
Air Gap |  | 1.6 |  | No load amps |  |  |  | 29 | - |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 530 |  | No load watts |  |  |  | 6191 | - |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 13 |  | Impedance amps |  | 3 | f | 144 | - |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.051"x.289")x1 |  | Impedance volts |  | 3 | f | 1150 | - |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 3 | f | 29528 | - |  | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) | [6 empty] | Dry Kiln
Connection |  | 2 x Wye |  |  | Winding |  | 80/115 | 60 / 79 | -
MCL |  | 936 |  |  | Frame |  |  | - | -
Allowance for ins. depth |  | 10.2896 |  |  | Bearing PS/OS |  |  | - | -
Allowance for ins. width |  | 3.2594 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 26 x 1 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 92 |  | 598
Coil grouping |  | - |  |  |  | RPM |  | 1189
Coil pitch (slot number) |  | 1 ~ 11 |  |  |  | CODE |  | F
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 |  |  | Method of Connection
Resistance per phase @ 20 °C |  | 0.2765 |  |  |  | DESIGN |  | - |  |  | Skip
Coil Weight | Wire1 | 315.3 |  |  |  | Nom.Eff. (%): |  | - |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | -
FL / LR |  | 500 / 3038 | 424 / 200
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 559 | - | 607.6087
[6 empty] | LRT (%) | 60 | 126 | -
[6 empty] | BDT (%) | 175 | 258 | -
[6 empty] | SLIP (%) |  | 0.91 | -
[5 empty] | IEEE-B | Eff. (%) |  | 94.9 | -
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 86.3 | -
|  |  |  | Losses (Watts) |  | Primary |  | 8137 | -
[6 empty] | Secondary |  | 4998 | -
[6 empty] | Core |  | 3787 | -
[6 empty] | F & W |  | 1722 | -
[6 empty] | Stray |  | 9494 | -
End Ring (Reference) |  |  |  | Note | TOP HAT, WP II, Cu-Bar, A/F Brg.
|  |  |  | LINK: | H080431.RAT & LAB 0251.DAT
361-N133-3L2Y ; 362-N133-04
RSO2: 400-N209-04 ; 135-N206-101SS
LIMITS: DT6700U
Rev.3 create the 4000V package. Z.X 04/22/22
Approved | H.YAMAGA | Design | A. GRACIA |  | REV2. CHG INSULATION FROM EDS-C-1059
Date | 2003-08-08 | Date | 2003-08-08 |  | JERRY R 03/05/13
REV1. FIRST ISSUE
32.05
2.00
3.00
8.05
52.0
2.83
10.8
342.7
30.0
45.0
60.0
311-
411-
051-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 6 Pole - 700.0 HP - 1200 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 12000.0 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~121 | 125.1 | 22.5 | 1.544 | 556.5 | 533.8 | 881.8
121~243 | 125.3 | 11.4 | 1.392 | 550.9 | 472.5 | 715.4
243~364 | 125.6 | 7.0 | 1.336 | 544.5 | 443.7 | 610.5
364~485 | 126.1 | 7.2 | 1.331 | 536.8 | 431.2 | 533.2
485~606 | 126.9 | 11.3 | 1.370 | 527.8 | 430.0 | 471.6
606~728 | 128.3 | 18.6 | 1.443 | 517.3 | 436.6 | 415.6
728~849 | 131.2 | 28.5 | 1.542 | 504.9 | 446.7 | 358.6
849~970 | 138.9 | 43.1 | 1.652 | 488.8 | 453.6 | 294.2
970~1031 | 154.2 | 57.6 | 0.820 | 471.0 | 208.4 | 207.7
1031~1091 | 183.7 | 69.9 | 0.696 | 445.9 | 164.9 | 146.9
1091~1152 | 229.4 | 83.1 | 0.541 | 380.1 | 110.3 | 91.2
1152~1189 | 177.5 | 94.1 | 0.586 | 214.6 | 5.5 | 19.5
Acceleration Time: 14.3 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 4137 kW / s |  | 75°C |  | 150°C
Rotor Bar Rise | 4614 kW / s |  | 114°C |  | 228°C
End Ring Rise | 132 kW / s |  | 9°C |  | 18°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 7.1°C / s |  | 392.4 kW | 160°C | 22.5 s
Rotor Bar | 15.7°C / s |  | 634.6 kW | 260°C | 16.6 s
Rotor ER | 1.3°C / s |  | 18.1 kW | 180°C | 143.3 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 60°C + |  | 100°C + | 40°C | = 200°C | 14.1 s
Rotor Bar | 79°C + |  | 181°C + | 40°C | = 300°C | 11.6 s
Rotor ER | 79°C + |  | 101°C + | 40°C | = 220°C | 80.8 s
Cold Stall Time: | 36.9 s |  | Hot Stall Time: |  | 20.8 s
Note on F4: Xie, Zichao: NEMA inertia 6903 LB-ft^2

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | -
| TIC SR No.: | -
MOTOR NAMEPLATE DATA
| H.P.: | 700 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 1200
| FRAME: | 5812UZ |  | ENCL: | WP-II |  | FLAMPS: | 92 |  |  | FLRPM: | 1189
| FORM: | DCK4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | F |  |  | DUTY: | Cont.
| MODEL No.: | QUOTE#27078 |  |  |  |  | kW: | -
| NOM. EFF.: | 94.5 |  | MIN. EFF.: | - |  | P.F.: | 86
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 559 |  |  | FULL LOAD (lb-ft.): | 3092 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 125 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 255
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 94.9 | [5 empty] | FULL LOAD: | 86.3
|  | 3/4 LOAD: | 94.8 | [5 empty] | 3/4 LOAD: | 82.5
|  | 1/2 LOAD: | 94 | [5 empty] | 1/2 LOAD: | 73
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | Zichao Xie
[9 empty] | DATE: | 2022-04-22
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | QUOTE#27078 |  |  | FLAmps: | 92
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812UZ
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 425.9 lb-ft² | Date: | 2022-04-22
FLRPM: | 1189 | Load Inertia: | 12000.0 lb-ft² | File: | DT6700U
| Locked Rotor Amps: | 559 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 125% | Starting at: | FV (V)
| Breakdown Torque: | 255% | Accel. Time: | 14.3 (s)
| Rated Torque: | 3092 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | DT6700U
|  | Prepared by: | Zichao Xie | Checked by:
Load
100 | 0 | 0.37259 | 100
99.2 | 94.7449 | 106.6047 | 98.4
96 | 255 | 359.8984 | 89.75
90.9474 | 203.7391 | 466.3767 | 76.4632
85.8947 | 163.7202 | 503.0148 | 63.3263
80.8421 | 144.6803 | 520.9648 | 51.8526
70.7368 | 133.1995 | 541.5358 | 34.2526
60.6316 | 129.242 | 556.1254 | 22.6947
50.5263 | 127.4529 | 568.4694 | 14.4211
40.4211 | 126.4253 | 578.8962 | 8.2526
30.3158 | 125.8008 | 588.1543 | 6.0632
20.2105 | 125.3899 | 595.6414 | 7.9579
10.1053 | 125.1416 | 602.0676 | 14.9263
0 | 125 | 607.6087 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | QUOTE#27078 |  |  | FLAmps: | 92
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812UZ
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 425.9 lb-ft² | Date: | 2022-04-22
FLRPM: | 1189 | Load Inertia: | 12000.0 lb-ft² | File: | DT6700U
559 A
125%
3092 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | DT6700U
|  | Prepared by: | Zichao Xie | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
607.6087 | 35 | 15 |  | 607.6087 | 0.0001
600 | 35.8933 | 15.3828 |  | 604.8913 | 1.544
500 | 51.6864 | 22.1513 |  | 598.8043 | 2.936
400 | 80.7599 | 34.6114 |  | 591.8478 | 4.272
300 | 143.5732 |  |  | 583.4783 | 5.603
200 | 323.0398 |  |  | 573.6957 | 6.973
255 | 198.7173 | 85.1646 |  | 562.2826 | 8.416
180 | 408.9935 | 170.9205 |  | 548.8043 | 9.958
145 | 614.5822 | 263.3924 |  | 531.3043 | 11.61
125 |  | 600 |  | 511.9565 | 12.43
125 |  | 1200 |  | 484.6739 | 13.126
125 |  | 10000 |  | 413.1522 | 13.667
|  |  |  | 233.1088 | 14.253

## Performance
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | QUOTE#27078 |  |  | FLAmps: | 92
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 5812UZ
Pole: | 6 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 700 | Rotor Inertia: | 425.9 lb-ft² | Date: | 2022-04-22
FLRPM: | 1189 | Load Inertia: | 12000.0 lb-ft² | File: | DT6700U
| Locked Rotor Amps: | 559 A | Load Type: | Fan / Pump
| Locked Rotor Torque: | 125% | Starting at: | FV (V)
| Breakdown Torque: | 255% | Accel. Time: | 14.3 (s)
| Rated Torque: | 3092 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 1200 | 1400
[8 empty] | 1198 | 1260
Comments: | PROJECT | - |  | D.E.Curve #: | DT6700U |  |  | 1196 | 1120
[8 empty] | 1194 | 980
[8 empty] | 1192 | 840
[8 empty] | 1190 | 700
|  | Prepared by: | Zichao Xie | Checked by: |  | SYNC SPEED | 1200 | 1188 | 560
[6 empty] | NEW SPEED LOWER RANGE | 1180 | 1186 | 420
[6 empty] | NEW kW UPPER RANGE | 1400 | 1184 | 280
[8 empty] | 1182 | 140
[8 empty] | 1180 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 29 | 100 | 0.44221
25 | 90.7 | 49.8 | 41.73 | 86.5094 | 10.2842
50 | 94 | 73 | 54.93 | 73.0188 | 19.8438
75 | 94.8 | 82.4 | 72.36 | 59.0094 | 29.5065
100 | 94.9 | 86.3 | 92.06 | 45 | 39.3165
125 | 94.7 | 87.7 | 113.48 | 30.4712 | 49.2506
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 33.8974 | 100 | 11.136
25 | 90.6732 | 49.8112 | 41.7316 | 84.9956 | 10.2866
50 | 93.9918 | 73.0208 | 54.9243 | 72.1192 | 19.8468
75 | 94.7656 | 82.4698 | 72.3513 | 58.8835 | 29.5271
100 | 94.8534 | 86.3421 | 92.0566 | 45.2724 | 39.3331
125 | 94.6442 | 87.7505 | 113.4743 | 31.3143 | 49.275
1200
1198
1196
1194
1192
1190
1188
1186
1184
1182
1180
RPM
1400
700
560
420
280
140
Input Watts (kW)
840
980
1120
1260
EFF.
P.F.
RPM
AMPS
WATTS
0.0