## DesignSheet
TOSHIBA INTERNATIONAL CORPORATION | [7 empty] | Calc. Code: | 2-2-2-0-1-2
3-PHASE SQUIRREL CAGE INDUCTION MOTOR DESIGN SHEET | [8 empty] | B.L.-1 P.F.-1
File: | G:\DESPRO\RAT FILES\DT8M30U.rat |  |  |  |  | Date: | 2022-05-04 | Time: | 9:42
Pole | HP | RPM | Form | Voltage | Frequency | Temperature | FLSpeed | FLSlip | Frame
8 | 1500 | 900 | DCW4 | 4000 | 60 | 105 | 895.5 / 889.0 | 0.0050 / 0.0122 | 6813US
Core Data |  |  | Winding Data |  |  |  | Constant Data
| Primary | Secondary |  |  | Bar | End Ring | St. Slot Pitch | 26.3981 | LR Test Data
Air Gap | 1.9 | [5 empty] | Rt. Slot Pitch | 33.7272 | ES
Space Fac. | 0.93 |  | Pitch | 1 ~ 9 | Cross Section Area |  | Mean Value | 30.0626 | 736.854
Core Length | 994 | 994 |  |  | UB: 585.0 | UER: 1500.0 | Eff.T.W.St. | 16.4073 | WS
OD | 815 | 601.2 | Coil Pitch | 0.8888 |  |  | Eff.T.W.Rt. | 32.8157 | 45765.2945
ID | 605 | 300 | Slot Fill | - | EBL: 50.5 | ERD1: 501.0 | St.Carter Fac. | 1.2308 | IS
Core Depth | 49 | 103.05 | Con./Slot | 14 |  | ERT: 30.00 | Rt.Carter Fac. | 1.0278 | 197.0507
Eff.Core L. | 762.6 | 762.6 | Wire Size 1 | (.102"x.204")x2 | (13 x 45) | ERH: 50.00 | Carter Factor | 1.265 | Volts / Turn
Slot Data |  |  | Wire Size 2 | - |  |  | Short. Factor | 0.98478 | 27.4937
Number | 72 | 56 | // Circuits | 2 |  |  | Distrib. Factor | 0.95964 | AC
Kind | Open | Rectang | Connection | Wye |  |  | Wind. Factor | 0.94503 | 522.5208
Skew | - | 0 | MCL | 1464 | 1125 |  | Reactance | (Coeff.: 0.0530)
Depth | 56 | 47.55 | No.Cond./Ph. | 168 |  |  |  | Running | Start
Width | 9.99 - 9.99 | 13.05 | Res. (20°C) | 0.081669 |  |  | Stator Slot | 17.6122 | 17.6122
Opening | 14.4 | 3.5 | (105°C) | 0.10894 | 0.061962 | 0.0069914 | Rotor Slot | 18.8813 | 11.1142
Tip Depth | 2.83 | 2.5 | Material | CU | CU | CU | Zigzag | 8.4519 | 5.5005
T.Min.Wid. | 11.9981 | 15.3478 | Spec.Resist. | 1.742 | 1.742 | 1.742 | Coil End | 3.7716 | Skew R.: 0.00
Low. R. | 0 | 0.8 | Spec.Gravity | 8.89 | 8.89 | 8.89 | Belt Leakage | 3.1223 | 2.2686
Up. R. | - | 0.8 | Weight (kg) |  |  |  | Total Resist. | 0.1779 | 0.39288
Wedge Dep. | 2.83 - 0.50 | Magnetic | Wire 1 | 344.1256 | 336.3781 | 46.1788 | Total React. | 2.7492 | 2.123
Duct | 29 x 6 | 29 x 6 | Wire 2 | - | - | - | Impedance | 2.755 | 2.159
Effective Depth (S=1) |  |  | Magnetic Circuit Data |  |  |  |  | Core Loss Data
| Res.= | 44.8812 |  | Length | Section | Density | AT | Volume | Loss |  | 887.8 | 125RPM |  | Kline/in2
| Reac.= | 45.0016 | Primary Core | 16.0025 | 747.348 | 14.6126 | 257.409 | 89923.0735 | 5897.873 |  | 889.0 | 100RPM |  | 94.2749
Excitation Data |  |  | Tooth | 5.6 | 823.4764 | 13.2617 | 58.7347 | 36891.7432 | 2067.7861 |  | 890.2 | 75RPM |  | 85.5594
Excit.Amps | 69.019 / 72.655 |  | Second.Core | 9.9372 | 1571.7186 | 6.9483 | 17.8804 | Total | 7965.6591 |  | 891.3 | 50RPM |  | 44.8275
Core Loss | 2.435 / 2.563 | Flux / Pole | Tooth | 4.755 | 819.2941 | 13.3294 | 51.0129 | C.L.C. | 1.75 / 1.02 |  | 892.1 | 25RPM |  | 85.9962
NoLoad | 69.06 / 72.70 | 10.9207 | Air Gap | 0.19 | 1540.1111 | 7.0909 | 1072.1203 | S.F.C. | 6.05 |  |  |  |  | 45.7474
Load Characteristics |  |  | Temp. Rise @ 100%: | 65 / 65 |  | No Load Loss | 23052.9 / 16200.0 | W.Loss | 13939.9 / 8094.4
Load (%) | 25 | 50 | 75 | 100 | 125 | Primary Loss | 12690.7 / 13305.0 | S.Loss | 2945.9 / 1710.6
Current (A) | 75.96 / 78.75 | 116.03 / 120.30 | 154.29 / 159.97 | 197.05 / 204.30 | 243.40 / 252.36 | Second. Loss | 5832.4 / 13428.0 | Total C.Loss | 16885.8 / 9805.0
Efficiency | 0.921 / 0.909 | 0.953 / 0.941 | 0.963 / 0.951 | 0.966 / 0.954 | 0.966 / 0.954 | Frict.& Wind. | 5000.0 / 4487.0 | Stray Loss | 13428.001 | 0.966 | 0.954 | 0.98758 | Eff.
P.F. | 0.577 / 0.564 | 0.730 / 0.713 | 0.815 / 0.797 | 0.849 / 0.829 | 0.859 / 0.839 | Starting Data |  | Slip | PF | 0.849 | 0.829 | 0.97644 | PF.
Slip | 0.0015 / 0.0088 | 0.0025 / 0.0097 | 0.0037 / 0.0109 | 0.0050 / 0.0122 | 0.0063 / 0.0135 | LRA | 1069.7 / 1413.8 |  |  | 197.05 | 204.30 | 1.0368 | Current
RPM | 898.6 / 892.1 | 897.8 / 891.3 | 896.7 / 890.2 | 895.5 / 889.0 | 894.3 / 887.8 | % | 542.8 / 717.5 |  |  | 895.5 | 889.0 | 0.99274 | RPM
L (Inv., MH) | 5.2744 | 5.2744 | 5.2744 | 5.2693 | 5.2267 | LRT (kg.m) | 1057.0 / 1704.0 |  | 0.18198
(No Load) | 5.2744 |  | Correlated to: DT8M30U_lab#1086_RM.dat |  |  | % | 86.8 / 140.0
Design Parameters (Full Load) |  |  |  | Magnetic Pull & Thrust |  | BDT (kW) | 2571.9531 | 0.025061 | 0.62172
IM/IW | 0.41104 | I*R1/E | 0.0092375 | Rosenberg | 1741.4317 | % | 228.7 / 240.0
IW*X/E | 0.19989 | I*R2/E | 0.0050134 | Schwisky | 3053.9271 | Amps | 582.1205 |  |  | HP0.95 | 1040.6069
SUM | 0.61092 | Friction/OP. | 0.0044683 | Tsurumi | 2448.6921 | Max. Output | 2508.3354 | 0.024417 | 0.63018 | HP1.5 | 58094.7502
IH/I | 0.012434 | Total | 0.031153 | Thrust (1mm) | 654.8358 | % | 224.1587 |  |  | (RPM/1000)2.4 | 0.77657
|  | Efficiency | 0.96885 | Thrust (3 mm) | 1363.388 | Amps | 574.5011 |  |  | (RPM/1000)1.8 | 0.82725
Single Cage Data | [5 empty] | Miscellaneous Data |  |  |  | A | 24
Slot Number | 56 | Slit Width | - | T.M.Wid.Low. | - | Watt Rad. | 0.083528 | Coil Cur. Density |  | k | 0.0685
Depth | 47.55 | Slit Depth | - | Cal.T.W.Up. | - | DG2L(cm2) | 296381.9808 | 3.76 / 3.89 |  | Hz | 60
Opening | 3.5 | L.S.Up.Wid. | - | Cal.M.T.Wid. | - | GD2L(kg.m2) | 374.9366 | Bar Cur. Den. |  | Load Inertia | 27349.4827
Tip Depth | 2.5 | L.S.Low.Wid. | - | Cal.M.T.Wid. | - | DO2L(cm2) | 544664.5 | UB: 2.44 / 2.53 | LB: -
Up. Sl. Wid. | 13.05 | L.S.Depth | - | X2S | - | IMC | 1 | ER Cur. Den.
Up. Sl. Dep. | - | T.M.Wid.Up. | - | X3S | - | Coil Pitch Ct. | 0.9166 | UER: 2.14 / 2.22 | LER: -
S-T Curve Data (Custom Values)
Slip | Torque (%) | Current (%) | Slip | Torque (%) | Current(%)
0 | 0 | 0.33854 | 0.69053 | 140.3499 | 676.8801
0.004 | 169.97 | 196.9227 | 0.79368 | 140.1447 | 683.2799
0.02 | 240 | 491.444 | 0.89684 | 140.0449 | 688.6051
0.071579 | 168.1949 | 551.6136 | 1 | 140 | 693.1373
0.12316 | 153.3844 | 576.267
0.17474 | 148.0063 | 594.5279 | Acceleration Data (FV V)
0.27789 | 144.6883 | 623.0236 | Load Type: | Fan / Pump
0.38105 | 142.6696 | 643.1153 | Load Inertia: | 4610.2 kg.m²
0.48421 | 141.4313 | 657.6093 | Accel. Time: | 8.5 (s)
0.58737 | 140.7338 | 668.5719 | Rated Torque: | 1217.1 kg.m
Load
100
99.2
95.25
81.3895
67.979
55.5579
36.7579
24.0842
15.2632
8.7579
6.1895
7.8737
14.7789
30

## Data Sheet
TOSHIBA INTERNATIONAL CORPORATION
INDUCTION MOTOR DATA SHEET
File: | DT8M30U | [5 empty] | HRW / Model Number: | M308WTQL11E-C
Type: TIKE - Form: DCW4 - 8 Pole - 1500 HP - 2300/4000 V - 60 Hz - 6813US - Class F | [12 empty] | Motor Type Selection | Electrical Steel Table
Motor Parameters |  |  |  | PERFORMANCE |  |  |  | DESIGN | TEST |  |  |  | EPACT | M22 - 26Ga.
Material |  | M36 - 26Ga. |  | NL & Impedance Test |  |  |  |  | Lab# 1086 |  |  |  | EQP-III | M36 - 26Ga.
Air Gap |  | 1.9 |  | No load amps |  |  |  | 73 | 72.79 |  |  |  | Exp.Prf. | NCB1 - 26Ga.
Stack length |  | 994 |  | No load watts |  |  |  | 16200 | 16200 |  |  |  | Exp.Prf.-EQPIII | M43 - 26Ga.
Number of turns per coil |  | 7 |  | Impedance amps |  | 1 | f | 308 | 206.3 |  |  |  | Prem. Eff. | M45 - 26Ga.
Wire 1 (size & number) |  | (.102"x.204")x2 |  | Impedance volts |  | 1 | f | 1150 | 904 |  |  |  | Standard Eff. | M54 - 26Ga.
Wire 2 (size & number) |  | - |  | Impedance watts |  | 1 | f | 45765 | 42000 |  |  |  | OWP | TIPA Lam
Slot fill - circle/square method (%) |  | - |  | Temperature Rise (°C) |  |  |  |  | RM | RTD |  |  | Dry Kiln
Connection |  | 2 x Delta / 2 x Wye |  |  | Winding |  | 80/115 | 65 / 86 | 64.6/85.4 | 87.2/115
MCL |  | 1464 |  |  | Frame |  |  | - | 34.7/
Allowance for ins. depth |  | 14.0988 |  |  | Bearing PS/OS |  |  | - | 36.2/43.5
Allowance for ins. width |  | 3.6368 |  |  | End Ring |  |  | - | -
Slot/Wire arrangement |  | 14 x 2 |  | Nameplate Data
Effective cross section for coil |  | - |  |  |  | FLC (A) |  | 353 / 204 | 205 |  | #VALUE!
Coil grouping |  | - |  |  |  | RPM |  | 889 | 889
Coil pitch (slot number) |  | 1 ~ 9 |  |  |  | CODE |  | H | H
Method of coil connection |  | - |  |  |  | S. F. |  | 1.15 | 1.15 |  |  | 353.3384 | Method of Connection
Resistance per phase @ 20 °C |  | 0.0817 |  |  |  | DESIGN |  | - |  |  |  |  | Skip
Coil Weight | Wire1 | 757.1 |  |  |  | Nom.Eff. (%): |  | 95.4 |  |  |  |  | Adjacent
(lbs.) | Wire2 | - |  |  |  | Min.Eff. (%): |  | - |  |  |  |  | -
Current Densities (A/cm2) |  |  | Bar / ER |  |  | P.F. (%): |  | 82.5
FL / LR |  | 389 / 2696 | 253 / 222
Stator Slot Shape (Reference) |  |  |  | Performance
[6 empty] | LRC (A) | - | 2449 / 1414 | 1413.8 |  | #VALUE!
[6 empty] | LRT (%) | 60 | 140 | 140
[6 empty] | BDT (%) | 175 | 240 | 240
[6 empty] | SLIP (%) |  | 1.22 | 1.19
[5 empty] | IEEE-B | Eff. (%) |  | 95.4 | 95.3
Rotor Slot Shape (Reference) | [5 empty] | PF (%) |  | 82.9 | 82.9
|  |  |  | Losses (Watts) |  | Primary |  | 13305 | 13305
[6 empty] | Secondary |  | 13428 | 13428
[6 empty] | Core |  | 9805 | 9805
[6 empty] | F & W |  | 4487 | 4487
[6 empty] | Stray(Assumed 1.2%) |  | 13428 | 13428
End Ring (Reference) |  |  |  | Note
|  |  |  | LINK: | DT8M30U.rat with DT8M30U_lab#1086_RM.dat
RSO2: 400TB41-01
TOP HAT ASSY: 135-M133-102
Approved |  | Design | A. Gracia
Date |  | Date | 2012-02-15 |  | Rev.1 update correlation per lab 1086. Z.X 05/04/22
REV1. ADDED 2300V DATA. JROD 08/18/2023
47.55
2.50
3.50
13.05
56.0
2.83
14.4
501.0
50.0
50.5
30.0
311-
411-
051-
Note on K4: Insert type of motor Either choose from list or write appropriate name
Note on D6: Choose Steel Type from list or input name
Note on D21: Choose Method of coil connection from list!

## LoginSheet
[8 empty] | P | T | L | T
PROJECT HISTORY | [7 empty] | E | D | I | Y | H
[8 empty] | R |  | M | P
[8 empty] | F |  | I | E
[9 empty] | C | T |  | I
[8 empty] | D | U |  | T | N
[8 empty] | A | R | R | E | S
[7 empty] | S | T | V | E | S | U
DATE | PROJECT | SMART NUMBER | QTY | CUSTOMER | REMARKS | LIMIT CODE | F | A | E | V | T | L
REVISION HISTORY
REV | REMARKS | [5 empty] | DATE |  |  | INIT

## StallTime
Rating: | 8 Pole - 1500.0 HP - 900 RPM - 4000 V - 60 Hz
Starting Performance
Load Type: Fan / Pump - 27349.5 lb-ft²
RPM | Motor | Load | Accel. | Line | Stator | Rotor
Speed Increment | Torque (%) | Torque (%) | Time (s) | Amps | kW / s | kW / s
0~93 | 140.0 | 22.4 | 0.862 | 1409.4 | 563.5 | 1199.1
93~186 | 140.1 | 11.3 | 0.787 | 1399.3 | 507.8 | 982.2
186~279 | 140.2 | 7.0 | 0.761 | 1387.4 | 483.4 | 841.1
279~371 | 140.5 | 7.5 | 0.762 | 1372.4 | 474.8 | 733.4
371~464 | 141.1 | 12.0 | 0.785 | 1352.7 | 477.6 | 644.9
464~557 | 142.1 | 19.7 | 0.828 | 1326.7 | 487.3 | 563.6
557~650 | 143.7 | 30.4 | 0.895 | 1291.5 | 503.5 | 483.3
650~743 | 146.3 | 46.2 | 1.012 | 1241.9 | 534.3 | 404.2
743~789 | 150.7 | 61.8 | 0.570 | 1194.2 | 274.2 | 293.0
789~836 | 160.8 | 74.7 | 0.589 | 1150.4 | 266.0 | 221.0
836~882 | 204.1 | 88.3 | 0.438 | 1063.9 | 181.2 | 104.7
882~896 | 205.0 | 97.2 | 0.146 | 702.1 | 47.9 | 44.9
896~900 | 135.0 | 99.6 | 0.111 | 271.3 | 1.5 | 24.2
Acceleration Time: 8.5 s
| Energy |  | First Start |  | Second Start
Stator Winding Rise | 4803 kW / s |  | 36°C |  | 73°C
Rotor Bar Rise | 5877 kW / s |  | 45°C |  | 91°C
End Ring Rise | 663 kW / s |  | 37°C |  | 75°C
Locked Rotor Thermal Capability
Cold Condition
| Rate of Rise |  | Power | Rise Limit | Max Time
Stator Copper | 5.7°C / s |  | 754.2 kW | 160°C | 28.1 s
Rotor Bar | 10.9°C / s |  | 1407.8 kW | 260°C | 23.9 s
Rotor ER | 8.9°C / s |  | 158.8 kW | 180°C | 20.1 s
Hot Condition
| Hot Temp. |  | Rise Limit | Ambient | Total | Max.Time
Stator Copper | 65°C + |  | 95°C + | 40°C | = 200°C | 16.7 s
Rotor Bar | 86°C + |  | 174°C + | 40°C | = 300°C | 16.0 s
Rotor ER | 86°C + |  | 94°C + | 40°C | = 220°C | 10.5 s
Cold Stall Time: | 42.6 s |  | Hot Stall Time: |  | 22.2 s

## Performance Data Sheet
TOSHIBA INTERNATIONAL CORPORATION | [8 empty] | INDEX |  | MPCF-1033
Industrial Division / Houston Motor Plant | [8 empty] | SHEET NO. |  | 1 of 1
[9 empty] | ISSUED |  | 7/31/13
[9 empty] | SUPERSEDES |  | 11/8/96
[9 empty] | REVISION |  | 2
SQUIRREL CAGE INDUCTION MOTOR | [8 empty] | WRITTEN BY |  | MDC
PERFORMANCE SPECIFICATIONS | [8 empty] | APPROVED BY |  | PAA
| CUSTOMER: | -
| TIC SR No.: | -
MOTOR NAMEPLATE DATA
| H.P.: | 1500 |  | VOLTS: | 4000 |  | 3 PH / | 60 Hz |  |  | S. RPM: | 900
| FRAME: | 6813US |  | ENCL: | WP-II |  | FLAMPS: | 204 |  |  | FLRPM: | 889
| FORM: | DCW4 |  | S.F.: | 1.15 |  | NEMA DESIGN: | - |  |  | INSUL CLASS: | F
| TYPE: | TIKE |  | AMB.: | 40°C |  | CODE: | H |  |  | DUTY: | Cont.
| MODEL No.: | M308WTQL11E-C |  |  |  |  | kW: | -
| NOM. EFF.: | - |  | MIN. EFF.: | - |  | P.F.: | -
AMPERAGE |  |  |  | TORQUES |  |  |  | **BEARINGS:
|  | LOCKED ROTOR: | 1414 |  |  | FULL LOAD (lb-ft.): | 8862 |  |  | DRIVE END: | REFER TO NP
[6 empty] | LOCKED ROTOR (%): | 140 |  |  | OPPOSITE DRIVE END: | REFER TO NP
[6 empty] | BREAK DOWN (%): | 240
EFFICIENCY | [6 empty] | POWER FACTOR
|  | FULL LOAD: | 95.4 | [5 empty] | FULL LOAD: | 82.9
|  | 3/4 LOAD: | 95.1 | [5 empty] | 3/4 LOAD: | 79.7
|  | 1/2 LOAD: | 94.1 | [5 empty] | 1/2 LOAD: | 71.3
ALL CHARACTERISTICS ARE AVERAGE EXPECTED VALUES BASED UPON RATED VOLTAGE,
FREQUENCY AND SINEWAVE POWER INPUT.
THE DECLARED LOCKED ROTOR CURRENT HAS A TOLERANCE OF 20%.
* TEMPERATURE RISE WILL BE CONSISTENT WITH INSULATION, AMBIENT AND SERVICE FACTOR AS
DEFINED BY NEMA-MG-12 OR -20.
** BEARINGS ARE THE ONLY RECOMMENDED SPARE PART(S).
[9 empty] | CERTIFIED BY: | JERRY R
[9 empty] | DATE: | 2023-08-18
- | 6205ZZ |  | 1 | -
TEFC | 6206UU |  | 1.15 | A
ODP | 6207ZZ |  |  | B
6208UU
6211ZZ
6211C3
6211ZZC3
6305UUC3
6306UUC3
6308C3
6308UU
6308ZC3
6309UU
6309UUC3
6309C3
6309C3XS
6309ZC3
6310ZZ
6310C3
6310C3XS
6310ZZC3
6312
6312C3
6312ZZ
6312ZZC3
6312C3XS
6313
6313ZZ
6313ZZC3
6313C3
6314
6314C3
6317
6317C3
6318
NU318
6318C3
NU318C3
6320
6320C3
NU322
NU322C3
NU324C3
NU324C3
6314C3XS
6317C3XS

## STCurve
TOSHIBA INTERNATIONAL CORPORATION
Speed Torque/Current Curve
Model #: | M308WTQL11E-C |  |  | FLAmps: | 204
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 6813US
Pole: | 8 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1500 | Rotor Inertia: | 2224.3 lb-ft² | Date: | 2023-08-18
FLRPM: | 889 | Load Inertia: | N/A | File: | DT8M30U
| Locked Rotor Amps: | 1414 A | Load Type: | N/A
| Locked Rotor Torque: | 140% | Starting at: | N/A
| Breakdown Torque: | 240% | Accel. Time: | N/A
| Rated Torque: | 8862 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | DT8M30U
|  | Prepared by: | JERRY R | Checked by:
Load
100 | 0 | 0.33854 | 100
99.6 | 169.97 | 196.9227 | 99.2
98 | 240 | 491.444 | 95.25
92.8421 | 168.1949 | 551.6136 | 81.3895
87.6842 | 153.3844 | 576.267 | 67.979
82.5263 | 148.0063 | 594.5279 | 55.5579
72.2105 | 144.6883 | 623.0236 | 36.7579
61.8947 | 142.6696 | 643.1153 | 24.0842
51.5789 | 141.4313 | 657.6093 | 15.2632
41.2632 | 140.7338 | 668.5719 | 8.7579
30.9474 | 140.3499 | 676.8801 | 6.1895
20.6316 | 140.1447 | 683.2799 | 7.8737
10.3158 | 140.0449 | 688.6051 | 14.7789
0 | 140 | 693.1373 | 30

## Thermdam
TOSHIBA INTERNATIONAL CORPORATION
Thermal Limit & Acceleration Curves
Design Values (For Reference Only)
Model #: | M308WTQL11E-C |  |  | FLAmps: | 204
Enclosure: | WP-II | Voltage: | 4000 V | Frame: | 6813US
Pole: | 8 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1500 | Rotor Inertia: | 2224.3 lb-ft² | Date: | 2023-08-18
FLRPM: | 889 | Load Inertia: | 27349.5 lb-ft² | File: | DT8M30U
1414 A
140%
8862 lb-ft
Comments: | PROJECT | - |  | D.E.Curve #: | DT8M30U
|  | Prepared by: | JERRY R | Checked by:
#DIV/0!
#DIV/0!
Current (%) | Cold | Hot |  | CURRENT (%) | Accel. Time
693.1373 | 35 | 15 |  | 693.1373 | 0.0001
600 | 46.7094 | 20.0183 |  | 690.8824 | 0.862
500 | 67.2615 | 28.8264 |  | 685.9314 | 1.649
400 | 105.0961 | 45.0412 |  | 680.098 | 2.41
300 | 186.8375 |  |  | 672.7451 | 3.172
200 | 420.3843 |  |  | 663.0882 | 3.957
240 | 291.9336 | 125.1144 |  | 650.3431 | 4.785
180 | 692.6239 | 222.4256 |  | 633.0882 | 5.68
145 | 799.78 | 342.7628 |  | 608.7745 | 6.692
125 |  | 700 |  | 585.3922 | 7.262
125 |  | 1400 |  | 563.9216 | 7.851
125 |  | 10000 |  | 521.5196 | 8.289
|  |  |  | 344.1667 | 8.435
|  |  |  | 132.7949 | 8.546

## Performance 4000V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | M308WTQL11E-C |  |  | FLAmps: | 204 A
Enclosure: | WP-II | Voltage: | 4000V | Frame: | 6813US
Pole: | 8 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1500 | Rotor Inertia: | 2224.3 lb-ft² | Date: | 2023-08-18
FLRPM: | 889 | Load Inertia: | N/A | File: | DT8M30U
| Locked Rotor Amps: | 1414 A | Load Type: | N/A
| Locked Rotor Torque: | 140% | Starting at: | N/A
| Breakdown Torque: | 240% | Accel. Time: | N/A
| Rated Torque: | 8862 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 900 | 4000
[8 empty] | 898 | 3600
Comments: | PROJECT | - |  | D.E.Curve #: | DT8M30U |  |  | 896 | 3200
[8 empty] | 894 | 2800
[8 empty] | 892 | 2400
[8 empty] | 890 | 2000
|  | Prepared by: | JERRY R | Checked by: |  | SYNC SPEED | 900 | 888 | 1600
[6 empty] | NEW SPEED LOWER RANGE | 880 | 886 | 1200
[6 empty] | NEW kW UPPER RANGE | 4000 | 884 | 800
[8 empty] | 882 | 400
[8 empty] | 880 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 73 | 100 | 0.405
25 | 90.9 | 56.4 | 78.75 | 82.8885 | 7.6929
50 | 94.1 | 71.3 | 120.3 | 73.111 | 14.8565
75 | 95.1 | 79.7 | 159.97 | 59.6667 | 22.083
100 | 95.4 | 82.9 | 204.3 | 45 | 29.3348
125 | 95.4 | 83.9 | 252.36 | 30.3333 | 36.6727
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 71.6033 | 100 | 23.3372
25 | 90.9455 | 56.3618 | 78.7535 | 60.3371 | 7.6878
50 | 94.1486 | 71.2822 | 120.3015 | 56.0974 | 14.8525
75 | 95.0906 | 79.6149 | 159.9653 | 50.526 | 22.0581
100 | 95.3914 | 82.8541 | 204.3021 | 44.7544 | 29.318
125 | 95.4113 | 83.8281 | 252.3581 | 38.8443 | 36.6399
900
898
896
894
892
890
888
886
884
882
880
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0.0

## Performance 2300V
TOSHIBA INTERNATIONAL CORPORATION
Performance Curve
Design Values (For Reference Only)
Model #: | M308WTQL11E-C |  |  | FLAmps: | 353 A
Enclosure: | WP-II | Voltage: | 2300 V | Frame: | 6813US
Pole: | 8 | Frequency: | 3 PH / 60 Hz | Ins. Class: | F
HP: | 1500 | Rotor Inertia: | 2224.3 lb-ft² | Date: | 2023-08-18
FLRPM: | 889 | Load Inertia: | N/A | File: | DT8M30U
| Locked Rotor Amps: | 2449 A | Load Type: | N/A
| Locked Rotor Torque: | 140% | Starting at: | N/A
| Breakdown Torque: | 240% | Accel. Time: | N/A
| Rated Torque: | 8862 lb-ft
[8 empty] | SPEED | KW
[8 empty] | 900 | 4000
[8 empty] | 898 | 3600
Comments: | PROJECT | - |  | D.E.Curve #: | DT8M30U |  |  | 896 | 3200
[8 empty] | 894 | 2800
[8 empty] | 892 | 2400
[8 empty] | 890 | 2000
|  | Prepared by: | JERRY R | Checked by: |  | SYNC SPEED | 900 | 888 | 1600
[6 empty] | NEW SPEED LOWER RANGE | 880 | 886 | 1200
[6 empty] | NEW kW UPPER RANGE | 4000 | 884 | 800
[8 empty] | 882 | 400
[8 empty] | 880 | 0
ADJUSTED
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 126.4397 | 100 | 0.405
25 | 90.9 | 56.4 | 136.399 | 82.8885 | 7.6929
50 | 94.1 | 71.3 | 208.3657 | 73.111 | 14.8565
75 | 95.1 | 79.7 | 277.0762 | 59.6667 | 22.083
100 | 95.4 | 82.9 | 353 | 45 | 29.3348
125 | 95.4 | 83.9 | 437.1003 | 30.3333 | 36.6727
ORIGINAL
Load | Efficiency | PF | Amps | RPM | Input Watts
0 |  |  | 71.6033 | 100 | 23.3372
25 | 90.9455 | 56.3618 | 78.7535 | 60.3371 | 7.6878
50 | 94.1486 | 71.2822 | 120.3015 | 56.0974 | 14.8525
75 | 95.0906 | 79.6149 | 159.9653 | 50.526 | 22.0581
100 | 95.3914 | 82.8541 | 204.3021 | 44.7544 | 29.318
125 | 95.4113 | 83.8281 | 252.3581 | 38.8443 | 36.6399
900
898
896
894
892
890
888
886
884
882
880
RPM
4000
2000
1600
1200
800
400
Input Watts (kW)
2400
2800
3200
3600
EFF.
P.F.
RPM
AMPS
WATTS
0.0